## Cover
STOP-IT project
Work package 4 - task 3
Risk Reduction Measures Database (RRMD)
Authors | Institution
Hans-Joachim Mälzer | IWW
Fabian Vollmer | IWW
Enric Bonet Gil | CETaqua
David Baquero | CETaqua
Jordi Meseguer | Aigues de Barceona / CETaqua
Carlos González Ortiz | Oylo
Mehdi Ahmadi | SINTEF

## Instructions for Use
Column | Guidance
Measure ID | In this column each measure is connected to a specific Measure ID. The ID is a consecutive number, which allows a clear identification of an event.
Short Name of Measure | For a facilitated recognition of and communication about the RRMs, here a short name for each measure is defined. The short names have to be written in CamelCase format.
Description | Here the idea and principle of the RRM is shortly described. General information is given which action is connected to the measure. It is helpful to use meaningful and informative notes to give the user a clear and fast understanding of the main working principle of the measure. Furthermore, the description should be as universal as possible to ensure a suitability of the measure in many cases with varying conditions, e.g. different countries, varying environmental conditions or similar. The description of a RRM might answer the following questions: • Which technique/method/kind of asset is used as RRM? • How does it work? • What is the overall aim of the measure? An example for a suitable description of a RRM is: Installation of security doors. Breaking into a room is prevented by installing massive and stable doors. The aim is to prevent unauthorized people to enter sensitive sites.
Type of Measure | The type of measure defines the main principle in which the measure reduces a risk. This categorization shall give the user a basic idea of the working principle of the measure.
Type of Source | In this category the origin of risk events for which the measure is able to reduce the risk is specified.
Type of Threat | The “Type of Threat” defines the nature of the reduced risk.
Type of Event | In this column the type of event treated by the measure is defined.
Specific Asset | Here it is defined, which specific asset is directly affected by the source of the reduced risk.
Type of Asset | The “Type of Asset” defines which type of asset is affected by the outcomes of the risk event for which the risk shall be reduced.
Consequence | The “Consequence” options define which consequence dimensions are affected if the treated risk event occurs.
Risk Reduction Mechanism | Here it is defined, if the frequency/likelihood, the consequences or both are reduced.
Characteristics of Action | In this column it is specified if a measure operates proactive, reactive or both. For example, the flushing of the piping system after an observed contamination is a reactive measure while the implementation of a functioning management system or the building of fences are proactive measures.
Comments | This column is supposed to be filled with notes or a short written text. Special properties of a measure like site specific features, advantages, disadvantages, experiences, additional explanations or similar might be entered.
Terms connected to affected risks | In this column several terms that are connected to the risk that shall be reduced by the risk reduction measure can be noted. Thus the search for suitable risk reduction measures might be facilitated. The possible terms for the list should be chosen from the ontology. The addition of terms in this field is optional, thus the user is free to leave this field empty.
Source / Literature | Here a source or reference to further information might be entered to enable the user to find more information about the measure if desired.

## Definitions
Type of Measure | [6 empty] | Type of Source | [5 empty] | Type of Threat |  |  | Type of Event |  |  |  | Specific Asset | [24 empty] | Type of Asset | [6 empty] | Consequence
Physical Barriers | Cyber Barriers | Redundancy | Control Systems | Consequence Mitigation | Economic Policy | Action and crisis management plans and training | External attacker | Internal attacker | Human fault | Natural phenomena | External supplier | Interdependant CI | Cyber | Physical | Cyber-Physical | Destruction | Interruption | Manipulation | Pollution | Additives | Control Center | Control System | Dosing system | Drinking water pipes | Drinking water tanks | Drinking water taps | Fire hydrants | Groundwater | Media Channels | Power transformer | Pressure boosting station | Pump | Sensor | Server | Spring water | Surface water | Transferred information | Transmission devices | Transmission pipes and equipment | Treatment unit process | Valve | Water under treatment | Well | Catchment area | Drinking water network | Drinking water tanks | Pressure boosting station | Raw water bodies | Raw water pipeline | Water abstraction point | Water treatment plants | Quantity | Quality | Financial | Reputation
Physical barriers reduce risks by featuring a barrier between the protected good and the risk source. It could e.g. be a fence to keep out unauthorized people from a sensitive site, bars at the windows, burglarproof doors, locks or similar. | Cyber barriers reduce risks by introducing a cyber-barrier between software or hardware components of a system like the process control/SCADA system and the risk source. This could for example be a firewall. Also encryption processes can be seen as cyber barriers as the encryption represents a barrier between the attacker and the sensitive content of the stolen data. | With the help of redundancies, risks based on the possibility of failing infrastructure, treatment equipment etc. shall be compensated. Redundant infrastructures (at least partially) keep on working in the desired manner if one of the redundantly constructed parts fails. Examples could be the construction of a second pipeline to ensure water supply if one of the pipelines is destroyed, mirrored (double) process control systems, additional pumping wells or additional treatment plants. | Risks can be reduced if a threat is recognized and indicated in an early stage before the negative consequence really occurs or before the negative consequences aggravate. Therefore, control systems can help to reduce the risk of unidentified incidents by warning the operating staff early enough to take action to prevent hazardous incidents from happening or aggravating. Examples for control systems are pressure sensors in pipes or alarm systems at water treatment sites. Generally, control systems consist of three main parts: the sensor, the evaluation of the measured data and the subsequent action. Control systems may work with physical/chemical sensors or human observations (inspections) to detect abnormal states of the supply system. The assessment of the observation may be done automatically by the control system or by human activity and will result in the decision if further action is necessary or not. The action can be carried out automatically by the control system or by human activity. Control systems may be used as a RRM against cyber, physical and cyber-physical threats. For cyber threats special software may be used as control system to prevent cyber-attacks. Control systems in the field of cyber threats are for example firewalls inspecting ingoing and outgoing data for viruses, Trojans or similar. However, sometimes it can be difficult to distinguish between control systems and barriers. For example, firewalls can be seen as barriers if they directly prevent access of malware to data, but they can also be seen as control systems if they just warn the user about potentially dangerous incidents. | The mitigation of consequences reduces the risk without having an impact on the probability or frequency of risk events occurring. Therefore, this kind of RRMs is suitable for the reduction of the negative consequences of risk events. Examples for consequence mitigation measures could be a) the construction of connection pipes to neighboring water supplier(s) to be prepared in a case such as the breakdown of the own water supply, b) the construction of wells for emergency supply or c) the signing of contracts with organizations providing small mobile emergency water treatment plants. | Financial risks can be reduced by building financial reserves or by contracting an insurance. Thus, the risk of insolvency or similar can be reduced, especially if a high amount of money will be necessary for the restauration of the water supply after an attack resulting in cost-intensive damages like damages to wells, pumps, networks, treatment plants or reservoirs. Economic Policy often may be seen also as a kind of Consequence Mitigation. | With appropriate action and crisis management plans and trainings, the staff of a water supply company can be taught how to behave and work in a way that the risk events like accidents and attacks are reduced to a minimum. Furthermore, also the correct behavior after the occurrence of a risk event might be taught to ensure the reduction of negative consequences to a minimum. In DIN EN 15975-1:2016-03 (Security of drinking water supply - Guidelines for risk and crisis management - Part 1: Crisis management) (2016) the main structures of a successful risk and crisis management for the security of drinking water supply are presented and might serve as an example for this category (e.g. the establishment of a crisis unit, the definition of hierarchies of decision during crises or the cooperation between suppliers and authorities). Training of the behavior of the staff of water supply companies in crisis situations and situations after attacks is one possible example for this type of measure. Giving advice to the population about the correct behavior in case of attacks or water shortages is also an important activity of this measure type (e.g. by preparation of flyers in advance or by broadcasting announcements). Action and crisis management plans and training often may be seen also as a kind of Consequence Mitigation. | An external attacker is any attacker that does not belong to the staff of the water utility. An external attacker carries out attacks intentionally. | An internal attacker belongs to the staff of the water utility. An internal attacker carries out attacks intentionally. | Hazards occurring due to human faults are not based on an intentional attack. Although they are characterized by wrong behavior of people (human failure), the person/people causing the hazard are not aware of their wrong behavior or at least have no intention to cause the hazard. | Natural phenomena are caused by natural processes like rain, floods, droughts or similar. They lie out of the sphere of human influence. However, also rising risks e.g. due to human induced climate change are considered as natural phenomena. | External suppliers are any contractual partners of the water utility that provide necessary goods, systems, software or similar to the utility. This could be for example the suppliers of additives, providers of software components, cloud operators or similar. However, suppliers that are designated as critical infrastructure (like suppliers of electrical energy) are not part of the term external supplier. | In contrast to the term external supplier, here all suppliers that are part of critical infrastructures themselves are considered. These are for example the suppliers of electrical energy, contractual partners in the financial and insurance business or providers of telecommunication services. | “The threat is a pure cyber-attack on the water supply system. The cyber-attack happens without any prior physical damage or manipulation of assets or technical devices of the water supply system and influences [for example] the process control/SCADA system. As a result of the cyber-attack, malfunctions and wrong control commands may occur, which may destroy assets and technical devices or may influence the water supply system (pressure, continuity, quality) in a negative way.” (Ostfeld et al. 2018) | “The threat is a physical attack on the water supply system. By the physical attack assets or technical devices of the water supply system will be damaged or manipulated. The physical attack may also destroy or damage sensors, data transmission lines or the process control/SCADA system in a way that the normal function is no longer possible.” (Ostfeld et al. 2018) | “The threat is a physical attack [e.g.] on sensors, data transmission lines and/or the process control/SCADA system. By the attack, the sensors, data transmission lines and/or the process control/SCADA system will be manipulated […]. Malfunctions may occur, which may destroy assets and technical devices or may influence the water supply system (pressure, continuity, quality) in a negative way.” (Ostfeld et al. 2018) | “Destruction may completely destroy or damage asset or technical devices in a way that the normal function is no longer possible. It may affect water quantity and water quality. Destruction may be the direct result of a physical attack[, a human fault or a natural phenomenon] as well as an indirect result of a cyber-attack.” (Ostfeld et al. 2018) | An interruption is characterized by a lack of supply with relevant inputs for the water treatment and supply (e.g. raw water, electrical energy, additives). Often the interruption does not lie in the sphere of influence of the water utility as electrical energy, additives or similar are supplied by external suppliers or interdependent critical infrastructures | “By manipulation the function of the water treatment system is affected without a destruction of assets or technical devices or a pollution by addition of substances which are not already used in the water treatment process. Manipulation may result in an inadequate water quantity (e.g. by affecting pressure or continuity) or water quality (e.g. by affecting the dosage of chemicals used for drinking water treatment). Manipulation may be the direct result of a physical attack as well as of a cyber-attack. As a reaction on a pollution by manipulation, affected assets may be switched off or isolated from the supply system, which may cause a secondary effect on water quantity (pressure, continuity).” (Ostfeld et al. 2018) | “Substances may be added to the raw water, the drinking water or the additives, which affect the drinking water quality in a negative way. Pollution may be the direct result of a physical attack. As a reaction on the pollution, affected assets may be switched off or isolated from the supply system, which may cause a secondary effect on water quantity (pressure, continuity).” (Ostfeld et al. 2018) | Additives are any substances that are intentionally added to the water under treatment to improve its final quality. | The control center is the central location of the water utility where for example the control system is implemented. Often this is also the point where e.g. disturbances can be reported by affected customers and where the whole process of water provision is coordinated. | The control system or SCADA system is the central system of the water utility that allows the surveillance and control of the whole water supply process, from the catchment over the treatment, storage and distribution to the handover point to the end-user or contractual partner. Measured data is converged in the control system where it is visualized for the operating staff. The operating staff has the possibility to adjust relevant process parameters manually via the control system. The control system is located in the control center. | The dosing system adds additives to the water under treatment. The amount of additives added to the water can be set manually in the control system by the operating staff or automatically based on sensor data providing information about the quality of the raw and treated water. | Drinking water pipes distribute the treated water from the water treatment plant to the end-user or contractual partner. | Drinking water tanks are built as storages for treated water. They might also have a function as pressure regulator in the network. | Drinking water taps are all installations that allow the withdrawal of drinking water from the drinking water network for drinking or household purposes. | Fire hydrants are used e.g. by the fire department to get water from the drinking water network for fire extinguishing purposes. | Groundwater is a subsoil raw water source. | Media channels are used by the water utility to communicate with the general public. These could be homepages, social media channels, press releases or similar. | Power transformers transform electrical energy from the distribution network to the desired voltage needed by the water utility. | Pressure boosting stations increase the pressure in the distribution network e.g. between different pressure zones. | Pumps are used to enable the water transport e.g. from the catchment area to the treatment plant or in the distribution network by increasing the pressure. | Sensors are transforming physical or chemical properties, constitutions or compositions e.g. into an electrical signal (often between 4-20mA). | A server is providing computational services to different clients. These services might be software applications, data, resources or similar. | Spring water is water coming from subsoil sources that naturally streams to the surface. | Surface water is water accessible at the surface in water bodies like rivers, lakes or similar. | Transferred information are all signals that are on their way from the transmitter to the receiver. These could be for example wireless signals, electrical signals transferred by wires but also physical information like letters on paper. | Transmission devices are all devices that transmit information to other devices and that not fall under any other option like servers or sensors. These could be for example server clients like laptops, computers, mobile devices or similar used by the staff. | Transmission pipes and equipment are the set of pipes and equipment such as pumping stations used and deployed to transport water from the drinking water treatment plant into the drinking water network. | The processes deployed in different units of drinking water treatment plant. | A valve is installed to enable the regulation of water transport. Simple valves types which can be used are either open or closed to enable/disable water transport but other construction types, for example pressure reduction valves (PRV), also belong to this category. | Water under treatment is all water that is modified in its quality parameters in a water treatment plant. | Wells enable the extraction of groundwater from subsoil sources. | “The water catchment area will comprise the catchment areas of groundwater wells, as well as of springs, the water body and inflows of reservoirs used for drinking water supply and the river upstream of the abstraction point of river water used for drinking water supply.” (Ostfeld et al. 2018) | “The drinking water […] network is the network of […] pipes which supplies water to the customers. A differentiation of individual pipes is not made. Manholes and valve chambers are also part of the […] network.” (Ostfeld et al. 2018) | “Drinking water tanks are all tanks in which drinking water is stored before distribution. Drinking water tanks may comprise tanks at ground level and elevated tanks as well as water towers. In addition, small inflow tanks for pumps or intermediate tanks in water treatment plants are to be considered as they might be vulnerable to pollutions too.” (Ostfeld et al. 2018) | “They may be located between Drinking water main pipes or in the distribution network and allow the supply of higher elevated regions with drinking water.” (Ostfeld et al. 2018) | The raw water bodies are the location from which the raw water is directly extracted. These might be groundwater bodies, lakes or similar. | The pipes used for transporting raw water from the source to the drinking water treatment plant. | “Under this type of asset, the wells and abstraction pumps of surface waters (dams, rivers, and springs) are summarized. If the water is abstracted by gravity pipelines, the entrance of water into the pipeline is to be considered as well (e.g. feed hopper, intake tower, spring building).” (Ostfeld et al. 2018) | “Drinking water treatment plants are considered as integral units. There is no specification made amongst the possible components of a plant (e.g. ozonation, flocculation, sedimentation, filtration, intermediate tanks and pumps, valves and sensors). Chemical or physical disinfection is considered as a treatment.” (Ostfeld et al. 2018) | “An event may lead to a disturbance of quantity of water supply. This may result in an insufficient availability of drinking water. In some areas and/or periods a supply is only possible with low pressure and/or discontinuity.” (Ostfeld et al. 2018) | “An event may lead to a disturbance of the quality of supplied water. This may result in chemical, biological or radiological aberrations from the usual quality. The aberrations may be of minor concern but may reach up to a poisoning of the customers.” (Ostfeld et al., 2018) | “During an event that leads to a disturbance of water quality or water quantity, the amount of distributed water and the turnover may decrease. Furthermore, actions to remove the causes and to re-establish the normal estate of water supply will be necessary, which will need financial resources.” (Ostfeld et al., 2018) | Consequences dimension for events that end up in a loss of reputation by the company.
Literature
Ostfeld, A. , E. Salomons, P. Smeets, C. Makropoulos, E. Bonet, J. Meseguer, H.-J. Mälzer, F. Vollmer, and R. Ugarelli. D3.2 Risk Identification Database (RIDB). STOP-IT, 2018.

## RRMD
| Short Name of Measure | Description | Type of Measure | Type of Source | Type of Threat | Type of Event | Specific Asset | Type of Asset | Consequence | Risk Reduction Mechanism | Characteristics of Action | Comments (Viability, Advantages, Disadvantages) | Terms connected to affected risks | More detailed information/ Source
M01 | FencesAndWalls | Construction of fences or walls around sensitive sites. By the construction of such physical barriers the entrance to sensitive sites is impeded. The aim is to ensure that no unauthorized personnel gets access to sensitive buidlings, assets or infrastructures. | Physical Barriers | External attacker | Cyber | Manipulation of the data | Sensors | Irrigation water | Quality | Frequency/Likelihood | Proactive | Which kind of fence and/or wall is chosen depends inter alia on the protection needs of the respective infrastructure/asset/building. Thus, before a fence or wall is built, a security concept (e.g. defining different security zones) could be set up to define which needs for perimeter protection exist in the respective cases.
[6 empty] | Denial of service | Early warning system for safe water reuse
M02 | MotionDetectors | Implementation of motion detectors. Thus the intrusion of unauthorized personnel to sensitive sites is automatically detected. The aim is to be able to react quickly to occuring intrusions. | Control System | External attacker | Physical | Destruction | Additives | Drinking Water Tanks | Quantity | Consequences | Proactive & Reactive | Different reactions are possible if a motion detector is triggered by an intruder. A silent alarm could be sent to the staff (thus the probability that the intruder is caught by the police could be increased) or a loud alarm sound could be started (this could lead to a flight of the intruder before he/she causes any more serious consequences).
|  |  | Consequence Mitigation | Internal attacker | Cyber-Physical | Manipulation | Control Center | Pressure Boosting Station | Quality
|  |  | Action and Crisis Management Plans and Training | Action and Crisis Management Plans and Training |  | Pollution | Control System | Water Treatment Plants | Financial
[7 empty] | Dosing System |  | Reputation
Pressure Boosting Station
Pump
Server
Transmission Devices
Treatment Unit Process
Water under treatment
M03 | CameraSurveillance | Surveillance of sensitive sites, buildings or assets with camera systems. Thus intruders are detected by the staff that is surveilling the monitors. The aim is to be able to react quickly to occuring intrusions or intrusion attempts and to be able to identify the attacker after an occuring attack. |  | External attacker | Cyber | Manipulation of the data | Sensors | Sewers or wastewater treatment plant | Quality | Consequences | Proactive & Reactive
|  |  |  | Human fault | Physical | Destruction | Early warning system for safe water reuse | Irrigation water | Not serious
|  |  |  | Internal attacker |  | Denial of service | Ds11 flow forecast
M04 | Patrols | Organization of regular or irregular patrols at sensitive sites, buildings and assets. Thus intruders shall be noticed and the investigated sites, buildings and assets are checked for any obvious damages or similar. The aim is to prevent malicious attacks and to ensure the functionality of the water supply system. | Control System | External attacker | Physical | Destruction | Additives | Catchment Area | Quantity | Frequency/Likelihood & Consequences | Proactive & Reactive | A positive side-effect of patrols might be the deterrent effect on potential attackers decreasing the likelihood of malicious attacks.
|  |  | Consequence Mitigation | Internal attacker | Cyber-Physical | Manipulation | Control Center | Drinking Water Tanks | Quality
|  |  | Action and Crisis Management Plans and Training | Human fault |  | Pollution | Control System | Pressure Boosting Station | Financial
[7 empty] | Dosing System | Raw Water Bodies | Reputation
[7 empty] | Drinking Water Tanks | Raw Water Pipeline
[7 empty] | Power Transformer | Water Abstraction Points
[7 empty] | Pressure Boosting Station | Water Treatment Plants
Pump
Server
Spring Water
Surface Water
Transmission Devices
Treatment Unit Process
Water under treatment
Well
M05 | FloodProtection | Implementation of flood protection measures. By the building of dams or object protection measures against floods the intrusion of flood water to sensitive sites shall be prevented. The aim is to prevent any assets or buildings from being damaged by flood water and to ensure an ongoing high water quality. | Physical Barriers | Natural phenomena | Physical | Destruction | Additives | Catchment Area | Quantity | Frequency/Likelihood | Proactive
[5 empty] | Cyber-Physical | Pollution | Control Center | Pressure Boosting Station | Quality
[7 empty] | Control System | Raw Water Bodies | Financial
[7 empty] | Dosing System | Water Abstraction Points
[7 empty] | Power Transformer | Water Treatment Plants
Pressure Boosting Station
Pump
Sensor
Server
Spring Water
Transmission Devices
Treatment Unit Process
Water under treatment
Well
M06 | BarredWindows | Protection of windows with bars. Thus intruders cannot enter a building by destroying a window. The aim is to ensure that only authorized personnel can enter sensitive objects or sites. | Physical Barriers | External attacker | Physical | Destruction | Control Center | Pressure Boosting Station | Quantity | Frequency/Likelihood | Proactive | It might be sufficient to implement bars at windows below the second floor as the height of all other windows could be a sufficient physical barrier.
[5 empty] | Cyber-Physical | Manipulation | Drinking Water Tanks | Water Treatment Plants | Quality
[6 empty] | Pollution | Pressure Boosting Station |  | Financial
[7 empty] | Water under treatment |  | Reputation
M07 | BinaryContacts | Implementation of binary contacts as alarm system at doors, windows or storage tanks. Thus the intrusion of unauthorized personnel to sensitive site is automatically detected. The aim is to be able to react quickly to occuring intrusions. | Control System | External attacker | Physical | Destruction | Sensors | Sewers or wastewater treatment plant | Not serious | Consequences | Proactive | Different reactions are possible if a binary contact is triggered by an intruder. A silent alarm could be sent to the staff (thus the probability that the intruder is caught by the police could be increased) or a loud alarm sound could be started (this could lead to a flight of the intruder before he/she causes any more serious consequences).
|  |  | Consequence Mitigation | Internal attacker |  |  | Ds11 flow forecast
M08 | SecureDoorsAndWindows | Construction of doors and windows with a sufficient resistance class. Thus the time and effort that an attacker needs to overcome the respective barrier is increased. The aim is to gain more time to detect an attack and to react on the attack, furthermore the attractivity for an attack is reduced. | Physical Barriers | External attacker | Physical | Destruction | Control Center | Drinking Water Tanks | Quantity | Frequency/Likelihood | Proactive | An appropriate resistance class for doors and windows of specific buildings depends on the security zone that the building is assigned to. |  | DIN EN 1627 Türen, Fenster, Vorhangfassaden, Gitterelemente und Abschlüsse - Einbruchhemmung - Anforderung und Klassifizierung; Deutsche Fassung EN 1627:2011. Deutsche Norm. Berlin: Beuth Verlag GmbH.
|  |  |  | Internal attacker | Cyber-Physical | Manipulation | Drinking Water Tanks | Pressure Boosting Station | Quality
[6 empty] | Pollution | Power Transformer | Water Treatment Plants | Financial
[7 empty] | Pressure Boosting Station |  | Reputation
Server
Transmission Devices
Transmission Pipes and Equipment
Treatment Unit Process
Water under treatment
M09 | EntranceAccessControl | Implementation of an access control system for entrances to sensitive sites. Thus it shall be avoided that unauthorized people get access to the sensitive sites. The aim is to protect the infrastructures of the water utility from damages. | Physical Barriers | External attacker | Physical | Destruction | Control Center | Drinking Water Tanks | Quantity | Frequency/Likelihood | Proactive | The physical access control can be implemented in different forms. The most common way of access control is the distribution of keys or access cards for sensitive sites only to authorized personnel. Another way of access control would be the implementation of regularly changing codes that are necessary to open doors. Also the access permission via biometric data like fingerprints is possible. In case of biometric entrance systems special attention has to be paid to data protection issues. Access control can also be realized by personnel that is positioned at entrances to check access permissions manually. The principle of minimum access permissions should be applied, that means that as few access authorizations as possible should be distributed.
|  |  | Control System | Internal attacker | Cyber-Physical | Manipulation | Drinking Water Tanks | Pressure Boosting Station | Quality
|  |  |  | Human fault |  | Pollution | Power Transformer | Water Treatment Plants | Financial
[7 empty] | Pressure Boosting Station |  | Reputation
Server
Transmission Devices
Transmission Pipes and Equipment
Treatment Unit Process
Water under treatment
Well
M10 | SecureLocks | Installation of secure locks. Thus the picking of locks is substantially complicated. The aim is to prevent that attackers can easily enter sensitive sites by picking locks. | Physical Barriers | External attacker | Physical | Destruction | Additives | Drinking Water Tanks | Quantity | Frequency/Likelihood | Proactive
|  |  |  | Internal attacker |  | Manipulation | Control Center | Pressure Boosting Station | Quality
[6 empty] | Pollution | Dosing System | Water Abstraction Points | Financial
[7 empty] | Drinking Water Tanks | Water Treatment Plants | Reputation
Power Transformer
Pressure Boosting Station
Server
Transmission Devices
Transmission Pipes and Equipment
Treatment Unit Process
Water under treatment
M11 | DiscreetAppearance | If possible, sensitive sites and buildings should be designed in a discreet appearance. Thus it shall be avoided that the sites or areas raise awareness of potential attackers. The aim is to lower the probability of attacks. | Physical Barriers | External attacker | Physical | Destruction | Sensors | Sewers or wastewater treatment plant | Quality | Frequency/Likelihood | Proactive | An example for a discreet design could be pumping stations. The building in which the pumps are located should not directly indicate that this is a pumping station for drinking water so that potential attackers are directly aware of a potential attack point. Also areas on a water utility's properties where for example servers or the control center are located should not be directly recognisable. This would quickly indicate an attractive attack point for a potential intruder.
|  |  |  | Human fault |  | Discharge of pollutants | Alert system | Raw water bodies | Not serious
|  |  |  | Internal attacker |  |  | Ds11 flow forecast
M12 | SupervisionOfExternals | Supervision of any external people entering the water utility or sensitive sites. Any people who enter sites and who are not part of the utility's staff are supervised and not left alone at any time. Thus any data thefts, manipulations or similar shall be prevented. | Control System | External attacker | Physical | Destruction | Additives | Drinking Water Tanks | Quantity | Frequency/Likelihood | Proactive |  |  | Federal Office for Information Security: ORP.1: Organisation. In: IT-Grundschutz-Kompedium. 1st Edition. Bundesanzeiger Verlag GmbH, Cologne, 2018. P. 4
|  |  |  | External supplier | Cyber-Physical | Manipulation | Control Center | Pressure Boosting Station | Quality
[6 empty] | Pollution | Control System | Water Abstraction Points | Financial
[7 empty] | Dosing System | Water Treatment Plants | Reputation
Drinking Water Tanks
Power Transformer
Pressure Boosting Station
Pump
Sensor
Server
Transmission Devices
Transmission Pipes and Equipment
Treatment Unit Process
Valve
Water under treatment
Well
M13 | SmokeDetectors | Installation of smoke detectors. Thus fires are immediately noticed by the present staff. The aim is to protect all employees and infrastructures from serious injuries or damages caused by fire. | Control System | External attacker | Physical | Destruction | Additives | Drinking Water Tanks | Quantity | Frequency/Likelihood & Consequences | Proactive
|  |  | Consequence Mitigation | Internal attacker | Cyber-Physical |  | Control Center | Pressure Boosting Station | Quality
|  |  |  | Human fault |  |  | Drinking Water Tanks | Water Treatment Plants | Financial
|  |  |  | Natural phenomena |  |  | Power Transformer
Pressure Boosting Station
Pump
Server
Transmission Devices
Transmission Pipes and Equipment
Treatment Unit Process
M14 | ContainmentStructures | Construction of containment structures at sensitive locations like roads or airports. Thus raw water contaminations due to traffic accidents, leakages or similar are kept away from raw water sources for drinking water production. The aim is to ensure the constant and sufficient availability of raw water of a sufficient quality for drinking water production. | Physical Barriers | Human fault | Physical | Pollution | Groundwater | Catchment Area | Quality | Frequency/Likelihood
[7 empty] | Spring Water | Raw Water Bodies | Financial
Surface Water
M15 | RawWaterPipelineProtection | Physical protection of raw water transmission pipeline and equipment (pumps, valves,…). The aim is to protect the water transmission pipes against corrosion, intrusion, failure, etc. | Physical Barriers | External attacker | Physical | Destruction | Pump | Raw Water Pipeline | Quality | Frequency/Likelihood | Proactive & Reactive | This measure includes for example regular inspections of the raw water pipelines.
|  |  | Redundancy | Human fault | Cyber-Physical | Manipulation | Transmission Pipes and Equipment | Water Abstraction Points | Quantity
|  |  | Control System | Natural phenomena |  | Pollution |  |  | Reputation
|  |  | Action and Crisis Management Plans and Training | [5 empty] | Financial
M16 | SourceWaterQualityControl | Control of raw water quality. The aim is to control the raw water quality in order to select the best treatment process and operation. | Control System | External attacker | Physical | Pollution | Groundwater | Catchment Area | Quality | Frequency/Likelihood & Consequences | Proactive & Reactive
|  |  | Consequence Mitigation | Human fault |  |  | Spring Water | Raw Water Bodies
|  |  |  | Natural phenomena |  |  | Surface Water | Water Treatment Plants
Well
M17 | WatershedProtection | Pollution sources in the watershed may affect raw water quality. The aim is to control the activities within the watershed affecting raw water quality. | Physical Barriers | Human fault | Physical | Pollution | Groundwater | Catchment Area | Quality | Frequency/Likelihood | Proactive | One of the objectives of the Water framework directive is to protect the drinking water sources. Part of this measures could be inspections of the watersheds and regulations of human activities in the watershed (especially regulations of traffic, industry, agriculture, residential areas).
|  |  | Control System | Natural phenomena |  |  | Spring Water | Raw Water Bodies | Financial
|  |  | Consequence Mitigation | External attacker |  |  | Surface Water | Water Abstraction Points
|  |  | Economic Policy |  |  |  | Well | Water Treatment Plants
M18 | InflowAndBackflowPrevention | Implementation of inflow and backflow prevention devices at relevant points of the network (e.g. house connections, fire hydrants). Thus the contamination of the drinking water network via these sources is prevented. The aim is to prevent intentional and unintentional contaminations so that a high water quality is ensured. | Physical Barriers | External attacker | Physical | Pollution | Drinking Water Taps | Drinking Water Network | Quality | Frequency/Likelihood | Proactive
|  |  |  | Human fault |  |  | Fire Hydrants |  | Financial
Reputation
M19 | FiltersInAerationProcesses | All air for aeration purposes in water treatment plants and water storage tanks should be filtered. Thus it is aimed to prevent contaminations induced by entering air by the provision of physical barriers. The aim is to ensure an ongoing high quality of the supplied water. | Physical Barriers | External attacker | Physical | Pollution | Drinking Water Tanks | Drinking Water Tanks | Quality | Frequency/Likelihood | Proactive | Filters should be installed at every air intake for aeration purposes. Furthermore, no openings for aeration purposes should be built directly over the water surface to prevent that attackers can easily induce dangerous substances or that dangerous substances are induced in a natural way.
|  |  |  | Internal attacker |  |  | Treatment Unit Process | Water Treatment Plants | Financial
|  |  |  | Natural phenomena |  |  | Water under treatment |  | Reputation
M20 | PressureAndFlowSensors | Installation of pressure and flow sensors at different positions in the water distribution network. Thus it can be checked if the network is operated in the desired conditions. The aim is to ensure a water supply in sufficient quantity and pressure. | Control System | External attacker | Cyber | Destruction | Control System | Drinking Water Network | Quantity | Frequency/Likelihood & Consequences | Proactive | With this measure failures in the distribution network due to intended attacks like destructions of pumps or pipes might be detected. Furthermore, also failures due to naturally occuring damages like pipe breakages are detected (induced by natural phenomena or by wrong operation/human fault).
|  |  |  | Internal attacker | Physical | Manipulation | Drinking Water Pipes | Drinking Water Tanks | Financial
|  |  |  | Human fault | Cyber-Physical |  | Drinking Water Tanks | Raw Water Pipeline | Reputation
|  |  |  | Natural phenomena |  |  | Pressure Boosting Station | Water Abstraction Points
Pump
Transferred Information
Transmission Pipes and Equipment
Valve
M21 | OscillationSensors | Installation of oscillation sensors at pumps. Thus any imminent damages of the pump or manipulations of the pump operation or settings are detected by changed oscillation patterns. The aim is to ensure an ongoing proper pump functionality and to detect any manipulations. | Control System | External attacker | Cyber | Destruction | Pump | Pressure Boosting Station | Quantity | Frequency/Likelihood & Consequences | Proactive & Reactive | This measure might indicate imminent pump failures due to wear or intended pump manipulations which are not detected in another way because the signal of the pump status to the control center was manipulated to show the desired values.
|  |  | Consequence Mitigation | Internal attacker | Physical | Manipulation |  |  | Financial
|  |  |  | Natural phenomena | Cyber-Physical
M22 | ValvePositionSensors | Installation of sensors indicating the position of valves. Thus it can be checked if all valves are are in the position that they are obliged to. The aim is to check if the operating parameters are performed as they should or if any malfunctions or manipulations of the valves exist. | Control System | External attacker | Cyber | Manipulation | Control System | Drinking Water Network | Quantity | Consequences | Proactive
|  |  |  | Internal attacker | Physical |  | Transferred Information | Raw Water Pipeline | Financial
|  |  |  | Natural phenomena | Cyber-Physical |  | Transmission Devices | Water Treatment Plants
Valve
M23 | LevelSensors | Installation of sensors indicating the filling level of storage tanks or additive reservoirs. Thus it can be supervised if any storage tanks or reservoirs are running dry or overflow. The aim is to ensure a desired filling level in all reservoirs and storage tanks. | Control System | External attacker | Cyber | Destruction | Additives | Drinking Water Tanks | Quantity | Frequency/Likelihood | Proactive
|  |  |  | Internal attacker | Physical | Manipulation | Control System | Water Treatment Plants | Financial
|  |  |  | Human fault | Cyber-Physical |  | Drinking Water Tanks
|  |  |  | Natural phenomena |  |  | Pressure Boosting Station
Pump
Transferred Information
Transmission Pipes and Equipment
Valve
M24 | AutomatedValveControl | Automated control of valves to regulate required pressures and flows. Thus human errors e.g. leading to pressure shocks are avoided. The aim is to ensure ongoing desired conditions in the network and to protect the infrastructure from damages. | Control System | Human fault | Physical | Destruction | Drinking Water Pipes | Drinking Water Network | Quantity | Frequency/Likelihood | Proactive | Although the control of valves is automated, the possibility of a manual control should be given at every point of time.
[7 empty] | Transmission Pipes and Equipment | Raw Water Pipeline | Financial
Valve
M25 | OperatingParameterSurveillance | Surveillance of operating parameters from the catchment to the final distribution point. Thus any damages, malfunctions or manipulations in the supply chain are directly detected. The aim is to enable fast reactions to damages, malfunctions or manipulations. | Control System | External attacker | Cyber | Destruction | Control System | Drinking Water Network | Quantity | Consequences | Proactive | Potential parameters to be supvervised are volume flows and pressures of water at different positions in the system, pressure losses (e.g. at filters), membrane permeabilities or volume flows and pressures of air at aerations. The surveillance can be realized manually or automatically by the definition of certain allowed operating ranges.
|  |  | Consequence Mitigation | Internal attacker | Physical | Manipulation | Dosing System | Drinking Water Tanks | Quality
|  |  |  | Human fault | Cyber-Physical |  | Drinking Water Pipes | Pressure Boosting Station | Financial
|  |  |  | Natural phenomena |  |  | Drinking Water Tanks | Raw Water Pipeline | Reputation
[7 empty] | Pressure Boosting Station | Water Abstraction Points
[7 empty] | Pump | Water Treatment Plants
Server
Transferred Information
Transmission Devices
Transmission Pipes and Equipment
Treatment Unit Process
Valve
M26 | ProcedureForPersonnelChanges | Following of a structured procedure in case of new employees entering the company or employees leaving the company. Thus new employees directly learn about all important information security issues and leaving employees are informed about their duty of confidentiality. By this measure, data losses due to leaving employees and faults due to unawareness of new employees shall be prevented. | Action and Crisis Management Plans and Training | External attacker | Cyber | Denial of service | Web server | Digital solution users | Health issues | Frequency/Likelihood | Proactive | For new employees checklists should be used to ensure that no important issues about information security are forgotten. If possible, the leaving employee should train the new employee. All access rights have to be taken from the leaving employee. |  | Federal Office for Information Security: ORP.2: Personal. In: IT-Grundschutz-Kompedium. 1st Edition. Bundesanzeiger Verlag GmbH, Cologne, 2018. P. 3
|  |  |  | Internal attacker | Physical | Manipulation of the data | Sensors | Sewers or wastewater treatment plant | Quantity
|  |  |  | Human fault |  | Spoofing | Web application | Raw water bodies | Quality
[6 empty] | Manipulation | Alert system |  | False information
[6 empty] | Discharge of pollutants | Serious game |  | Reputation
[7 empty] | Ds 13 interface |  | Information leak
Ds11 flow forecast
Early warning system for bathing water quality
Ml based early warning system for bathing water
Server
M27 | EmployeesTrainings | Regular trainings, seminars, updates and informations on security issues should be implemented for all employees. Thus the staff is always kept up to date about any security relevant developments, behavioural rules and acute risks, both in the cyber and in the physical sector. The aim is to prevent hazards occuring due to unawareness and human faults. | Action and Crisis Management Plans and Training | External attacker | Human failure | Denial of service | Early warning system for safe water reuse | Sewers or wastewater treatment plant | Cso | Frequency/Likelihood & Consequences | Proactive & Reactive |  |  | Federal Office for Information Security: ORP.2: Personal. In: IT-Grundschutz-Kompedium. 1st Edition. Bundesanzeiger Verlag GmbH, Cologne, 2018. P. 4
|  |  |  | Internal attacker | Cyber | Manipulation of the data | Web server | Csos data quality | Health issues
|  |  |  | Operator | Physical | Missing data | Sensors | Sewer system | Quantity
|  |  |  | Human fault |  | Spoofing | Web application | Irrigation water | Quality
[6 empty] | Manipulation | Alert system | Digital solution users | False information
[6 empty] | Discharge of pollutants | Cloud | Raw water bodies | Financial
[7 empty] | Ds 13 interface |  | Damage to stakeholder activtiy
[7 empty] | Serious game |  | Reputation
[7 empty] | Ds11 flow forecast |  | Information leak
Early warning system for bathing water quality
Ml based early warning system for bathing water
Match-making tool
Mobile sensor (temperature, conductivity)
Server
Temperature sensor web-platform
M28 | SecurityCheckOfEmployees | Security check of new employees. By checking relevant data of new employees like the completeness of the CV and the criminal record, the confidentiality and reliability of the potential employee is checked. The aim is to employ trustworthy and reliable employees to ensure a safe operation. | Control System | External attacker | Cyber | Denial of service | Web server | Digital solution users | Health issues | Frequency/Likelihood | Proactive | The possibilities for security checks are significantly limited by different laws and regulations in the field of data protection. Therefore it has to be ensured that all information gaining processes are lying in the frame of legally allowed and ethically justifiable investigations.
|  |  | Action and Crisis Management Plans and Training | Internal attacker | Physical | Manipulation of the data | Sensors | Sewers or wastewater treatment plant | Quantity
|  |  |  | Human fault |  | Destruction | Web application | Csos data quality | Quality
[6 empty] | Spoofing | Alert system | Raw water bodies | False information
[6 empty] | Manipulation | Serious game |  | Financial
[6 empty] | Discharge of pollutants | Ds 13 interface |  | Not serious
[7 empty] | Ds11 flow forecast |  | Reputation
[7 empty] | Early warning system for bathing water quality |  | Information leak
Ml based early warning system for bathing water
Temperature sensor web-platform
Server
M29 | EmergencyPlans | Setting up of emergency plans. Thus clear responsabilities, courses of action, procedures and contacts are defined and documented for emergency cases. The aim is to reduce the consequences after serious cyber, physical or cyber-physical incidents. | Consequence Mitigation | External attacker | Cyber | Manipulation of the data | Sensors | Digital solution users | Health issues | Consequences | Proactive & Reactive | A complete crisis plan should exist including responsabilities, pending tasks, important contacts etc. All tasks from the evaluation of the situation over the determination of appopriate reactions to the crisis until the final realization of the actions and their effectiveness check have to be defined. Therefore also an emergency service must exist. |  | DIN EN 15975-1: Sicherheit der Trinkwasserversorgung - Leitlinien für das Risiko- und Krisenmanagement - Teil 1: Krisenmanagement; Deutsche Fassung EN 15975-1:2011+A1:2015. Deutsche Norm. Berlin: Beuth Verlag GmbH.
|  |  | Action and Crisis Management Plans and Training | Human fault | Physical | Discharge of pollutants | Alert system | Raw water bodies | Quality
[6 empty] | Denial of service | Early warning system for bathing water quality |  | False information
[7 empty] | Ml based early warning system for bathing water |  | Reputation
[7 empty] | Server |  | Information leak
M30 | RedundantAssetsAndInfrastructures | Constructions of redundant infrastructures and assets along the whole water supply chain. Thus the failure of one component can, at least partially, be compensated by the respective redundant asset. The aim is to ensure a constant supply of water with adequate quantity, quality and pressure. | Redundancy | Operator | Human failure | Denial of service | Early warning system for safe water reuse | Sewers or wastewater treatment plant | Cso | Consequences | Proactive | Redundant infrastructures could exist in the water extraction (wells, river extractions, reservoir extractions, spring water), water treatment infrastructures (filtration, adsorption, aeration, sedimentation, softening), water storage (tanks), water distribution (main pipes, distribution pipes, pressure boosting station) or similar infrastructures. Another kind of redundancy implementation that might make sense is the cooperation with other suppliers e.g. with neighbouring municipalities in supply networks.
|  |  | Consequence Mitigation | External attacker | Cyber | Manipulation of the data | Web server | Csos data quality | Quantity
|  |  |  | External supplier | Physical | Destruction | Sensors | Sewer system | Quality
|  |  |  | Internal attacker |  | Missing data | Web application | Irrigation water | False information
|  |  |  | Human fault |  | Spoofing | Alert system | Digital solution users | Financial
[6 empty] | Discharge of pollutants | Cloud | Raw water bodies | Not serious
[7 empty] | Ds 13 interface |  | Reputation
[7 empty] | Serious game |  | Information leak
Ds 12 decision support system
Ds11 flow forecast
Early warning system for bathing water quality
Match-making tool
Mobile sensor (temperature, conductivity)
Server
Temperature sensor web-platform
M31 | DistributedEnergySupply | Supply of energy from more than one supplier. Thus a potential supply failure of one electrical energy supplier can quickly be replaced by the supply of the redundant supplier. The aim is to prevent downtimes due to a lack of electrical energy. | Redundancy | Interdependent CI | Cyber | Interruption | Control Center | Drinking Water Network | Quantity | Consequences | Proactive
|  |  | Consequence Mitigation |  | Physical |  | Control System | Drinking Water Tanks | Quality
[5 empty] | Cyber-Physical |  | Dosing System | Pressure Boosting Station | Financial
[7 empty] | Pressure Boosting Station | Water Abstraction Points | Reputation
[7 empty] | Media Channels | Water Treatment Plants
Power Transformer
Pressure Boosting Station
Pump
Sensor
Server
Transmission Devices
Transmission Pipes and Equipment
Treatment Unit Process
Valve
M32 | EmergencyGenerators | Installation of emergency generators. Thus a complete failure of external energy supply can be compensated by the emergency generators. The aim is to prevent downtimes due to a lack of electrical energy. | Redundancy | External attacker | Physical | Interruption | Control Center | Drinking Water Network | Quantity | Consequences | Proactive
|  |  | Consequence Mitigation | Internal attacker | Cyber-Physical |  | Control System | Drinking Water Tanks | Quality
|  |  |  | Natural phenomena |  |  | Dosing System | Pressure Boosting Station | Financial
|  |  |  | Interdependent CI |  |  | Pressure Boosting Station | Water Abstraction Points | Reputation
[7 empty] | Media Channels | Water Treatment Plants
Power Transformer
Pressure Boosting Station
Pump
Sensor
Server
Transmission Devices
Transmission Pipes and Equipment
Treatment Unit Process
Valve
M33 | AdditionalStorageCapacity | Construction of additional storage tanks. Thus periods of water scarcity can be bridged easier due to a higher amount of stored water. The aim is to ensure a constant supply with drinking water also in times of reduced raw water avilability or attacks on water treatment or supply elements. | Redundancy | Internal attacker | Cyber | Spoofing | Web application | Sewers or wastewater treatment plant | Quantity | Consequences | Proactive
|  |  | Consequence Mitigation |  |  |  | Ds 13 interface
M34 | WaterIntakeAdaption | Re-designing of water intakes for periods of raw water scarcities. Thus the usual sources for raw water can also be used in case of low water levels e.g. by the construction of pumps, modified water intakes or additional wells. The aim is to ensure a constant supply with raw water. | Consequence Mitigation | Natural phenomena | Physical | Interruption | Groundwater | Catchment Area | Quantity | Frequency/Likelihood | Proactive
[7 empty] | Spring Water | Raw Water Bodies | Financial
[7 empty] | Surface Water | Water Abstraction Points
Well
M35 | WaterQualityOnlineSurveillance | Surveillance of the water composition along the supply chain by online sensors. Thus degradations of water quality (from raw water to the point of supply) are early detected. The aim is to enable fast reactions and the potential isolation of affected network parts or infrastructures. | Control System | External attacker | Physical | Pollution | Additives | Catchment Area | Quality | Consequences | Reactive | The quality should be checked with respect to chemical, microbiological and physical parameters. Potential parameters can for example be taken from existing laws or guidelines defining the required drinking water quality, examples are temperatures, pH values, conductivities, oxygen concentrations, turbidities, UV absorption or redox potential.
|  |  | Consequence Mitigation | Internal attacker |  |  | Control System | Drinking Water Network | Financial
|  |  |  | Human fault |  |  | Dosing System | Drinking Water Tanks | Reputation
|  |  |  | Natural phenomena |  |  | Drinking Water Tanks | Raw Water Bodies
[7 empty] | Fire Hydrants | Water Abstraction Points
[7 empty] | Groundwater | Water Treatment Plants
Spring Water
Surface Water
Water under treatment
Well
M36 | WaterTreatmentControl | Implementation of monitoring, treatment and disinfection processes in order to comply with the water quality standards under all circumstances. | Redundancy | External attacker | Physical | Destruction | Additives | Catchment Area | Quantity | Frequency/Likelihood & Consequences | Proactive & Reactive | This is a measure for process control & optimization.
|  |  | Control System | Internal attacker | Cyber-Physical | Interruption | Control System | Raw Water Bodies | Quality
|  |  | Action and Crisis Management Plans and Training | Human fault |  | Manipulation | Dosing System | Water Abstraction Points | Financial
|  |  |  | Natural phenomena |  | Pollution | Drinking Water Tanks | Water Treatment Plants | Reputation
|  |  |  | External supplier |  |  | Pump
|  |  |  | Interdependent CI |  |  | Sensor
Treatment Unit Process
Water under treatment
M37 | WaterQualityOfflineSurveillance | Offline monitoring of water quality parameters in the distribution systems to comply with the water quality standards under all circumstances. | Control System | External attacker | Physical | Destruction | Drinking Water Pipes | Drinking Water Network | Quantity | Frequency/Likelihood & Consequences | Proactive & Reactive
|  |  | Consequence Mitigation | Internal attacker | Cyber-Physical | Interruption | Drinking Water Tanks | Drinking Water Tanks | Quality
|  |  | Action and Crisis Management Plans and Training | Human fault |  | Manipulation |  |  | Financial
|  |  |  | Natural phenomena |  | Pollution |  |  | Reputation
External supplier
M38 | MonitoringAndControlOfDistributionSystem | Monitoring and controlling the distribution system for biofilms, deposits and corrosion. | Control System | Natural phenomena | Physical | Interruption | Additives | Drinking Water Network | Quantity | Frequency/Likelihood & Consequences | Proactive & Reactive
|  |  | Consequence Mitigation | Human fault |  | Pollution | Dosing System | Drinking Water Tanks | Quality
|  |  | Action and Crisis Management Plans and Training |  |  |  | Drinking Water Pipes | Water Treatment Plants | Financial
Drinking Water Tanks
Drinking Water Taps
M39 | WaterNetworkInterventionsForWaterSupplyRecovery | There are many events that potentially may lead to anomalies affecting the physical elements of the water network (i.e. pipe breakdown). When this occurs, a segment of the network containing the faulty element is isolated for its repair. This isolation may affect the supply of certain demand nodes in terms of quantity and pressure. Then, a set of network interventions must be enabled in order to recover the water supply service in the affected area during this emergency period. In general, this interventions aims to enable new water pathways to the affected area and/or adapting PRVs and pumping strategies to recover pressure assuring enough autonomy in the water tanks. | Physical Barriers | External attacker | Physical | Destruction | Drinking Water Pipes | Drinking Water Network | Quantity | Consequences | Reactive
|  |  | Redundancy | Internal attacker | Cyber-Physical | Interruption | Drinking Water Tanks | Drinking Water Tanks | Quality
|  |  | Control System | Human fault |  | Manipulation | Pressure Boosting Station | Pressure Boosting Station | Reputation
|  |  | Consequence Mitigation | Natural phenomena |  | Pollution | Pump
|  |  |  | External supplier |  |  | Valve
Interdependent CI
M40 | AdditivesQualityCheck | Supervision of quality of delivered additives. Thus the use of additives produced with substandard quality or the use of subsequently (intentionally or unintentionally) polluted additives is prevented. The aim is to prevent the pollution of drinking water caused by the use of polluted additives. | Control System | External attacker | Physical | Pollution | Additives | Water Treatment Plants | Quality | Frequency/Likelihood | Proactive
|  |  |  | External supplier |  |  |  |  | Financial
Reputation
M41 | InfrastructureAndAssetInspections | Regular and/or continuous inspections of existing infrastructure and assets by trained and professional personnel. Thus existing or impending damages, failures or manipulations are early detected. The aim is to undo damages, failures or manipulations to prevent more serious consequences on existing infrastructures. | Control System | External attacker | Cyber | Manipulation | Control System | Drinking Water Network | Quantity | Consequences | Reactive | The inspections shall detect intended manipulations of the assets and infrastructure by attackers as well as existing and imminent damages or failures due to wrong operation or wear.
|  |  | Consequence Mitigation | Internal attacker | Physical |  | Dosing System | Drinking Water Tanks | Quality
|  |  |  | Human fault | Cyber-Physical |  | Drinking Water Pipes | Pressure Boosting Station | Financial
|  |  |  | Natural phenomena |  |  | Drinking Water Tanks | Raw Water Pipeline | Reputation
[7 empty] | Power Transformer | Water Abstraction Points
[7 empty] | Pressure Boosting Station | Water Treatment Plants
Pump
Sensor
Server
Transmission Devices
Transmission Pipes and Equipment
Treatment Unit Process
Valve
Well
M42 | InformationSecurityGuidelines | Establishment of a guideline for information security. This guideline contains all relevant aspects about the company's information security aims and underlying processes. Thus the employees are aware of the importance of information security procedures and know how to behave to ensure information security. | Action and Crisis Management Plans and Training | External attacker | Cyber | Manipulation | Control System | Drinking Water Network | Quantity | Frequency/Likelihood | Proactive | The guideline(s) should contain information about the importance of information security, the security objectives, the most important aspects of the security strategy as well as the organisational structure established for information security. A clear scope must be defined. All employees must be informed about the guideline on information security. The guideline should regularly be updated. |  | Federal Office for Information Security: ISMS.1: Sicherheitsmanagement. In: IT-Grundschutz-Kompedium. 1st Edition. Bundesanzeiger Verlag GmbH, Cologne, 2018. P. 5
|  |  |  | Internal attacker | Cyber-Physical |  | Media Channels | Drinking Water Tanks | Quality
|  |  |  | Human fault |  |  | Sensor | Pressure Boosting Station | Financial
|  |  |  | External supplier |  |  | Server | Raw Water Pipeline | Reputation
[7 empty] | Transferred Information | Water Abstraction Points
[7 empty] | Transmission Devices | Water Treatment Plants
M43 | InformationSecurityManagementSystem | Implementation of an Information Security Management System (ISMS). The ISMS enables the implementation and continuous application of a thought out and effective information security process. The aim is to provide a general concept for a continuosly updated information security in a water utility. | Action and Crisis Management Plans and Training | Internal attacker | Cyber | Spoofing | Web application | Sewers or wastewater treatment plant | Quantity | Frequency/Likelihood | Proactive | An ISMS should be tailored to the existing management structures of the specific water utility. Due to different conditions existing in each site and utility, there cannot be one ISMS fitting as general system for all utilites. Thus there is a need of customization in each case. |  | Federal Office for Information Security: ISMS.1: Sicherheitsmanagement. In: IT-Grundschutz-Kompedium. 1st Edition. Bundesanzeiger Verlag GmbH, Cologne, 2018. Pp. 1-8
Ds 13 interface
M44 | PasswordSecurity | Access to sensitive and critical cyber applications, databases, control tools or similar should be protected by secure passwords. Thus only authorized people get access to the respective cyber space. The aim is to prevent attacker's access by hacking and to ensure the cyber system's integrity. | Cyber Barriers | External attacker | Cyber | Manipulation | Web applicaton | Digital solution users | Health issues | Frequency/Likelihood | Proactive | For the access to any application, database or similar a different password has to be used. Passwords should not be too short (at least 8 symbols) and contain symbols of different kinds (e.g. capital and small letters, special symbols, numbers). Passwords should be changed regularly. |  | Federal Office for Information Security: Passwords. Link: https://www.bsi-fuer-buerger.de/BSIFB/DE/Empfehlungen/Passwoerter/passwoerter_node.html Last access: 21.01.2019
|  |  | Control System | Human fault |  | Manipulation of the data | Web server | Sewers or wastewater treatment plant | Quantity
|  |  |  | Internal attacker |  |  | Cloud | Sewer system | Quality
[7 empty] | Web application | Raw water bodies | False information
[7 empty] | Serious game |  | Damage to stakeholder activtiy
[7 empty] | Alert system |  | Reputation
[7 empty] | Mobile apps to communicate bathing water quality |  | Information leak
Ds11 flow forecast
Ml based early warning system for bathing water
Match-making tool
Mobile sensor (temperature, conductivity)
Server
M45 | TwoFactorAuthentification | Implementation of two-factor authentification for especially sensitive applications. Thus the possibility of unauthorized access to sensitive applications is significantly reduced. The aim is to ensure a special protection for especially sensitive applications. Try not using SMS but dedicated apps instead (or dongles). | Cyber Barriers | External attacker | Cyber | Manipulation of the data | Web applicaton | Digital solution users | Health issues | Frequency/Likelihood | Proactive | Possible realizations for a two-factor authentification could for example be individual codes that are sent via SMS or TAN generators. |  | Federal Office for Information Security: Passwords. Link: https://www.bsi-fuer-buerger.de/BSIFB/DE/Empfehlungen/Passwoerter/passwoerter_node.html Last access: 21.01.2019
|  |  | Control System | Human fault |  |  | Web application | Sewers or wastewater treatment plant | Quantity
[7 empty] | Mobile apps to communicate bathing water quality |  | Quality
[7 empty] | Ds11 flow forecast |  | False information
[7 empty] | Match-making tool |  | Damage to stakeholder activtiy
[7 empty] | Server |  | Reputation
Information leak
M46 | RestrictedAccesToITSystem | The company must to restrict the network control actions and information accesibility to particular actors inside the company using a particular protocol acces (double factor). A security level of accessibility should be defined according to the person or group in charge of specific tasks in the company. | Cyber Barriers | External attacker | Cyber | Denial of service | Cloud | Sewers or wastewater treatment plant | Health issues | Frequency/Likelihood | Proactive
|  |  | Control System | Internal attacker |  | Manipulation of the data | Web platorm (berlin) | Operator | Quantity
|  |  |  | External supplier |  | Spoofing | Mobile apps to communicate bathing water quality | Csos data quality | Quality
|  |  |  | Human fault |  | Manipulation | Ds11 flow forecast | Sewer system | False information
[6 empty] | Eavesdropping | Well-diary | Irrigation water | Financial
[7 empty] | Web server | Digital solution users | Damage to stakeholder activtiy
[7 empty] | Web application | Raw water bodies | Reputation
[7 empty] | Temperature sensor web-platform |  | Information leak
Ds 13 interface
Mobile sensor (temperature, conductivity)
Temperature sensor web-platform
Web applicaton
Server
Early warning system for safe water reuse
Sensors
Serious game
Alert system
Match-making tool
Ml based early warning system for bathing water
M47 | NonManipulationConnectionTool | The company must forbid the network connection to not authorized mobile devices (PC, laptop, etc.). | Physical Barriers | Internal attacker | Cyber | Spoofing | Web application | Sewers or wastewater treatment plant | Quantity | Frequency/Likelihood | Proactive
|  |  | Cyber Barriers |  |  |  | Ds 13 interface
Control System
M48 | CryptographicProcesses | Implementation of cryptographic processes. Thus any relevant data is encrypted and therfore unreadable for an attacker. The aim is to ensure that any attacker getting access to sensitive data cannot read the data due to its encryption. | Cyber Barriers | External attacker | Cyber | Manipulation | Well-diary | Sewers or wastewater treatment plant | Health issues | Consequences | Proactive | Additionally to the data encryption, the possibility of encrypting also communication connections should be checked in dependence on the necessary effort for encryption and its practicability. The source and integrity of used cryptographic keys should also be checked. The keys should be changed in a sufficient frequency. Encryptions can be realized for transferred data (wireless connections, wires, mobile storage devices) and for data stored on servers, clients, mobile devices or similar. |  | Federal Office for Information Security: CON.1: Kryptokonzept. In: IT-Grundschutz-Kompedium. 1st Edition. Bundesanzeiger Verlag GmbH, Cologne, 2018. Pp. 1-6
|  |  | Consequence Mitigation | Internal attacker |  | Manipulation of the data | Early warning system for safe water reuse | Operator | Quantity
|  |  |  | External supplier |  | Eavesdropping | Web applicaton | Csos data quality | Quality
[7 empty] | Web server | Sewer system | False information
[7 empty] | Sensors | Irrigation water | Financial
[7 empty] | Web application | Digital solution users | Damage to stakeholder activtiy
[7 empty] | Alert system | Raw water bodies | Reputation
[7 empty] | Serious game |  | Information leak
Web platorm (berlin)
Temperature sensor web-platform
Mobile apps to communicate bathing water quality
Ds11 flow forecast
Early warning system for bathing water quality
Ml based early warning system for bathing water
Match-making tool
Temperature sensor web-platform
Server
M49 | DataBackups | All relevant data should be saved in a data backup regularly. Due to redundant data storages the loss of one data set can be compensated by using the backup data. Thus the ongoing operability of the utility is ensured. | Redundancy | External attacker | Human failure | Missing data | Cloud | Digital solution users | Cso | Consequences | Proactive | All relevant factors of influence on the process of data backup generation must be documented, e.g. the amount and time of changed data, availability requirements or similar. If applied, the requirements for online data backups, e.g. in clouds, must be determined (e.g. location of storage, methods of authentification, etc.). The backup data should be encrypted, furthermore the location of the backup data should not be the same as the location of the original data. |  | Federal Office for Information Security: CON.3: Datensicherungskonzept. In: IT-Grundschutz-Kompedium. 1st Edition. Bundesanzeiger Verlag GmbH, Cologne, 2018. Pp. 2-4
|  |  | Consequence Mitigation | Operator | Cyber | Denial of service | Mobile sensor (temperature, conductivity) | Sewer system | Reputation
Serious game
Web server
M50 | NetworkSeparation | Secure installation and operation of different network security zones. Thus unauthorized entries into sensitive networks can be complicated. The aim is to ensure the integrity, authenticity and confidentiality of all data in the network. | Physical Barriers | External attacker | Cyber | Spoofing | Early warning system for safe water reuse | Sewers or wastewater treatment plant | Quality | Frequency/Likelihood | Proactive | This measure is dealing with the IT networks. The complete network setup, structure, changes or similar must be documented in detail. The network must be separated into different security zones (e.g. internal network, demilitarized zone [DMZ], external connections [including untrustworthy networks like the internet]). Different security zones should also be physically separated. Firewalls must separate the security zones. Clients and server must be located in different segments of the network. Sensitive information must be transferred by using state-of-the-art secure protocols.
|  |  | Cyber Barriers | External supplier |  | Manipulation | Cloud | Sewer system | Reputation
|  |  | Control System | Internal attacker |  | Manipulation of the data | Web application | Raw water bodies | Quantity
|  |  |  | Human fault |  |  | Ds 13 interface | Irrigation water
Ds11 flow forecast
Ml based early warning system for bathing water
Mobile sensor (temperature, conductivity)
Server
M51 | AppropriateLayingOfWires | Information transmitting wires should be laid in a security conform way. Thus the probability of data thieveries and damages of wires is reduced by preventing unauthorized access to the data transmission wire. The aim is to protect sensitive data. | Physical Barriers | External attacker | Cyber-Physical | Destruction | Transferred Information | Drinking Water Network | Quantity | Frequency/Likelihood | Proactive | It should be made difficult to get access to wires e.g. by underground laying of wires, the protection of wires by mantles or similar.
|  |  |  | Internal attacker |  | Manipulation | Transmission Devices | Drinking Water Tanks | Quality
[8 empty] | Pressure Boosting Station | Financial
[8 empty] | Raw Water Pipeline | Reputation
Water Abstraction Points
Water Treatment Plants
M52 | ServerRoomSetup | Appropriate setup of server rooms. Thus the lifetime of servers is extended and its ongoing functionality is ensured. The aim is to ensure the continuous operability of all servers under appropriate conditions. | Physical Barriers | External attacker | Cyber-Physical | Destruction | Server | Drinking Water Network | Quantity | Frequency/Likelihood & Consequences | Proactive | The server room should be located apart from office rooms and ensure appropriate conditions (temperature, air humidity, constant electrical energy supply, etc.). The room should be secured by doors with an appropriate resistance class and with an appropriate access control system. Furthermore it should be protected against physical hazards like fire, water intrusion etc. A constant supply with electrical energy must be ensured, if necessary an Uninterruptable Power Supply (UPS) must be implemented. |  | Federal Office for Information Security: APP.3.3 Fileserver. In: IT-Grundschutz-Kompedium. 1st Edition. Bundesanzeiger Verlag GmbH, Cologne, 2018. Pp. 1-5
|  |  | Consequence Mitigation | Internal attacker |  | Interruption |  | Drinking Water Tanks | Quality
|  |  |  | Human fault |  | Manipulation |  | Pressure Boosting Station | Financial
|  |  |  | Natural phenomena |  |  |  | Raw Water Pipeline | Reputation
|  |  |  | Interdependent CI |  |  |  | Water Abstraction Points
Water Treatment Plants
M53 | MirroredSCADA | Implementation of a mirrored SCADA system. Thus in case of a failure of the SCADA system, this failure can be compensated by activating the mirrored SCADA system. The aim is to ensure an ongoing operability of the water utility. | Redundancy | External attacker | Cyber | Destruction | Control Center | Drinking Water Network | Quantity | Consequences | Proactive | The mirrored SCADA system should be not be located at the same position as the acutally used SCADA system.
|  |  | Consequence Mitigation | Internal attacker | Physical | Manipulation | Control System | Drinking Water Tanks | Quality
|  |  |  | Human fault | Cyber-Physical |  |  | Pressure Boosting Station | Financial
|  |  |  | Natural phenomena |  |  |  | Raw Water Pipeline | Reputation
Water Abstraction Points
Water Treatment Plants
M54 | DataIntegrityCheck | The integrity of important data should be checked e.g. by blockchain technology. Thus falsified signals are immediately detected. The aim is to ensure that any decision of the utility is based on data with ensured integrity. | Control System | External attacker | Cyber | Manipulation | Early warning system for safe water reuse | Sewers or wastewater treatment plant | Health issues | Frequency/Likelihood & Consequences | Proactive
|  |  |  | Internal attacker |  | Manipulation of the data | Web applicaton | Csos data quality | Quantity
|  |  |  | External supplier |  |  | Web server | Sewer system | Quality
[7 empty] | Sensors | Irrigation water | False information
[7 empty] | Web application | Digital solution users | Financial
[7 empty] | Alert system | Raw water bodies | Damage to stakeholder activtiy
[7 empty] | Serious game |  | Reputation
[7 empty] | Web platorm (berlin) |  | Information leak
Temperature sensor web-platform
Mobile apps to communicate bathing water quality
Ds11 flow forecast
Early warning system for bathing water quality
Ml based early warning system for bathing water
Match-making tool
Temperature sensor web-platform
Server
M55 | MalwareProtectionGuidelines | Implementation of guidelines for a correct behaviour to protect the IT systems from malware. Thus all employees know how to handle hard- and software to ensure a secure IT environment. The aim is to prevent any damages resulting from the malware and to ensure the integrity, authenticity and confidentiality of all data and assets in the IT infrastructure. | Control System | External attacker | Cyber | Manipulation | Control System | Drinking Water Network | Quantity | Frequency/Likelihood | Proactive | The guidelines should define the handling of potentially harmful soft- and hardware. It should e.g. be defined when and which storage devices may be connected to the IT infrastructure, how annexes of e-mails have to be handled and how executable files have to be treated.
|  |  | Action and Crisis Management Plans and Training | Internal attacker | Cyber-Physical |  | Media Channels | Drinking Water Tanks | Quality
|  |  |  | Human fault |  |  | Sensor | Pressure Boosting Station | Financial
[7 empty] | Server | Raw Water Pipeline | Reputation
[7 empty] | Transferred Information | Water Abstraction Points
[7 empty] | Transmission Devices | Water Treatment Plants
M56 | MalwareProtectionSoftware | Installation of suitable software to protect the IT systems against malware. By this measure malware reaching the IT system shall be blocked, deleted or at least directly noticed. Thus any damages resulting from the malware shall be avoided to ensure the integrity, authenticity and confidentiality of all data and assets in the IT infrastructure. | Cyber Barriers | External attacker | Cyber | Manipulation | Control System | Drinking Water Network | Quantity | Frequency/Likelihood | Proactive | Used applications and software for defense against malware should be tailored for the use in enterprises, solutions for home use are not sufficiently safe. Furthermore, the chosen solution should be updated and checked on its effectiveness regularly. The employees should be trained on handling possibly dangerous contents in a sensitive way. Any detections of malware should be reported directly by both, the user detecting the malware and automatically by the system. All relevant data emerging in the IT system should be logged for a fast detection of incidents and for an easier understanding of past attacks. |  | Federal Office for Information Security: OPS.1.1.4: Schutz vor Schadprogrammen. In: IT-Grundschutz-Kompedium. 1st Edition. Bundesanzeiger Verlag GmbH, Cologne, 2018. Pp. 3-5
|  |  | Control System | Internal attacker | Cyber-Physical |  | Media Channels | Drinking Water Tanks | Quality
|  |  | Consequence Mitigation | Human fault |  |  | Sensor | Pressure Boosting Station | Financial
[7 empty] | Server | Raw Water Pipeline | Reputation
[7 empty] | Transferred Information | Water Abstraction Points
[7 empty] | Transmission Devices | Water Treatment Plants
M57 | PatchAndChangeManagement | Implementation of a concept for the patch and change management in the IT environment. By following this concept, emerging security holes can be closed quickly and any (e.g. software) changes are monitored with regard to security issues. Thus the security of the IT systems of the company is ensured in general. | Cyber Barriers | External attacker | Cyber | Denial of service | Serious game | Digital solution users | Reputation | Frequency/Likelihood | Proactive | The concept should clearly define all responsabilites and procedures of the patch and changes management process. Furthermore, the handling of auto-updates that might be implemented in the used software should be regulated. |  | Federal Office for Information Security: OPS.1.1.3: Patch- und Änderungsmanagement. In: IT-Grundschutz-Kompedium. 1st Edition. Bundesanzeiger Verlag GmbH, Cologne, 2018. Pp. 3-5
|  |  | Control System | Internal attacker |  |  | Web server
Action and Crisis Management Plans and Training
M58 | NetworkTrafficAnalysis | Surveillance of all network traffic on suspicious patterns. Thus hacker attacks shall be recognized and negative consequences shall be prevented. The aim is to ensure the integrity, authenticity, confidentiality and operability of the network and all connected devices. | Control System | External attacker | Cyber | Spoofing | Early warning system for safe water reuse | Sewers or wastewater treatment plant | Health issues | Consequences | Proactive
|  |  | Consequence Mitigation | Human fault |  | Manipulation | Sensors | Csos data quality | Quantity
|  |  | Action and Crisis Management Plans and Training | Internal attacker |  | Manipulation of the data | Web application | Irrigation water | Quality
|  |  |  | External supplier |  | Denial of service | Alert system | Digital solution users | False information
[7 empty] | Ds 13 interface | Raw water bodies | Financial
[7 empty] | Ds 12 decision support system |  | Reputation
[7 empty] | Ds11 flow forecast |  | Information leak
Early warning system for bathing water quality
Ml based early warning system for bathing water
Match-making tool
Temperature sensor web-platform
Server
M59 | SecurityOfWirelessNetworks | Defitinition of security measures for the implementation and use of wireless network connections. Thus attacks on wireless connections shall be prevented. The aim is to ensure the integrity, autenticity, confidentiality and operability of the wireless network and all connected devices. | Cyber Barriers | External attacker | Cyber | Manipulation of the data | Sensors | Digital solution users | Quality | Frequency/Likelihood | Proactive | Before the implementation of wireless networks it must be checked if any other wireless networks exist in the same area with similar configurations that could disturb the implemented network. Generally accepted standards for authentification and encryption have to be used. All information transferred via wireless networks has to be encrypted with up-to-date encryption technologies. Access points must be located at positions where no unauthorized personnel can reach them. Access points may not be operated in default configurations. A security barrier should exist between wireless and wired connections. Regular checks for security wholes should be ensured. |  | Federal Office for Information Security: NET.2.1: WLAN-Betrieb. In: IT-Grundschutz-Kompedium. 1st Edition. Bundesanzeiger Verlag GmbH, Cologne, 2018. Pp. 1-6
|  |  | Action and Crisis Management Plans and Training |  |  | Denial of service | Early warning system for safe water reuse | Irrigation water | Quantity
Match-making tool
M60 | SoftwareManagement | The software management should be organized and carried out by responsible IT experts. Thus only credible software is installed correctly, furthermore an appropriate use of the software is teached to the staff. The aim is to avoid cyber security issues due to the installation of untrustful software, wrong installation of trustful software or inappropriate software uses. | Cyber Barriers | External attacker | Cyber | Spoofing | Web application | Digital solution users | Quality | Frequency/Likelihood | Proactive |  |  | Federal Office for Information Security: CON.4: Auswahl und Einsatz von Standardsoftware. In: IT-Grundschutz-Kompedium. 1st Edition. Bundesanzeiger Verlag GmbH, Cologne, 2018. Pp. 1-4
|  |  | Control System | External supplier |  | Denial of service | Ds 13 interface | Sewers or wastewater treatment plant | Reputation
|  |  | Action and Crisis Management Plans and Training | Internal attacker |  |  | Serious game |  | Quantity
Web server
M61 | MobileDeviceUsageRules | Setting up of clear rules for the use of mobile devices. Thus the staff knows how to use mobile devices outside the utility in a secure way. The aim is to ensure data and cyber security also outside of the utility area. | Action and Crisis Management Plans and Training | External attacker | Cyber | Manipulation | Transferred Information | Drinking Water Network | Quantity | Frequency/Likelihood & Consequences | Proactive | Examples for rules could be the mandatory use of privacy films for monitors or automatic screen locks after a certain time of inactivity. Losses of IT equipment should be reported as soon as possible to the utility. Portable devices should be encrypted. Connections to the utility's network should only be allowed via Virtual Private Network (VPN) connections. A list of mobile devices should exist in the company. |  | Federal Office for Information Security: CON.7: Informationssicherheit auf Auslandsreisen. In: IT-Grundschutz-Kompedium. 1st Edition. Bundesanzeiger Verlag GmbH, Cologne, 2018. Pp. 5-8
|  |  |  | Human fault | Cyber-Physical |  | Transmission Devices | Drinking Water Tanks | Quality
[8 empty] | Pressure Boosting Station | Financial
[8 empty] | Raw Water Pipeline | Reputation
Water Abstraction Points
Water Treatment Plants
M62 | DeletionAndDestructionOfDataCarriers | Ensuring of proper deletion of data and destruction of data carriers. By a proper deletion or destruction, the data shall be irreversibly wiped out. Thus the loss of any sensitive data shall be prevented. | Action and Crisis Management Plans and Training | External attacker | Cyber | Manipulation | Control System | Drinking Water Network | Quantity | Frequency/Likelihood | Proactive | The data deletion mechanisms should ensure that no data can be restored and that no residual data exist. All employees should be trained how to delete data and destroy data carriers correctly. If data carriers are collected and stored before destruction, the location of collection has to be protected against any possible intruders. |  | Federal Office for Information Security: CON.6: Löschen und Vernichten. In: IT-Grundschutz-Kompedium. 1st Edition. Bundesanzeiger Verlag GmbH, Cologne, 2018. Pp. 3-4
|  |  |  | Internal attacker | Cyber-Physical |  | Server | Drinking Water Tanks | Quality
|  |  |  | Human fault |  |  | Transmission Devices | Pressure Boosting Station | Financial
[8 empty] | Raw Water Pipeline | Reputation
Water Abstraction Points
Water Treatment Plants
M63 | SecureOutsourcing | Assurance of IT security in case of outsourcing by setting-up appropriate agreements with the respective companies. By these agreements it is guaranteed that also the respective external companies comply with the relevant security guidelines. Thereby it is ensured that emerging risks due to the outsourcing process are minimized. | Cyber Barriers | External attacker | Cyber | Spoofing | Web application | Digital solution users | Quality | Frequency/Likelihood & Consequences | Proactive | The agreement should ensure that the commissioned company complies with a sufficiently acknowledged security standard (e.g. the German IT-Grundschutz [IT-Basic Protection]). |  | Federal Office for Information Security: OPS.2.1: Outsourcing für Kunden. In: IT-Grundschutz-Kompedium. 1st Edition. Bundesanzeiger Verlag GmbH, Cologne, 2018. Pp. 3-6
|  |  | Control System | External supplier |  | Denial of service | Ds 13 interface | Sewers or wastewater treatment plant | Reputation
|  |  | Action and Crisis Management Plans and Training |  |  |  | Serious game
Web server
M64 | Documentation | A complete documentation of all relevant assets and processes in the physical and digital infrastructure of the water utility must be ensured. Thus a full overview of the utility and potential risks is available at any point of time. The aim is to be able to recognize any weak points that have to be treated by different risk redcution measures. | Control System | External attacker | Cyber | Denial of service | Serious game | Digital solution users | Reputation | Frequency/Likelihood & Consequences | Proactive & Reactive
|  |  | Action and Crisis Management Plans and Training |  |  |  | Web server
M65 | IdentificationClassificationAndRiskAssessmentTool | The Company must select a particular approach and methodology for risk assessment and analysis that incidents and prioritizes risks based on threats, vulnerabilities and consequences of security. | Physical Barriers | External attacker | Cyber | Destruction | Additives | Catchment Area | Quantity | Frequency/Likelihood & Consequences | Proactive & Reactive
|  |  | Cyber Barriers | Internal attacker | Physical | Interruption | Control Center | Drinking Water Network | Quality
|  |  | Redundancy | Human fault | Cyber-Physical | Manipulation | Control System | Drinking Water Tanks | Financial
|  |  | Control System | Natural phenomena |  | Pollution | Dosing System | Pressure Boosting Station | Reputation
|  |  | Consequence Mitigation | External supplier |  |  | Drinking Water Pipes | Raw Water Bodies
|  |  | Economic Policy | Interdependent CI |  |  | Drinking Water Tanks | Raw Water Pipeline
|  |  | Action and Crisis Management Plans and Training |  |  |  | Drinking Water Taps | Water Abstraction Points
[7 empty] | Fire Hydrants | Water Treatment Plants
Groundwater
Media Channels
Power Transformer
Pressure Boosting Station
Pump
Sensor
Server
Spring Water
Surface Water
Transferred Information
Transmission Devices
Transmission Pipes and Equipment
Treatment Unit Process
Valve
Water under treatment
Well
M66 | DDoS Protection | DDoS (Distributed Denial of Service) protection or mitigation is the process of protecting a target from a DDoS attack by using specialized network equipment or cloud based services. By using such a protection, the targeted company is able to mitigate the threat. | Cyber Barriers | External attacker | Cyber | Denial of service | Web server | Digital solution users | Quality
|  |  | Redundancy | Human fault |  |  | Sensors | Sewers or wastewater treatment plant | Reputation
|  |  |  | Internal attacker |  |  | Web application | Csos data quality | Financial
|  |  |  | External supplier |  |  | Alert system | Raw water bodies | Quantity
Serious game
Ds 13 interface
Ds 12 decision support system
Match-making tool
Temperature sensor web-platform
Server
M67 | Authenticity check | Implementing authenticity checks on the data provenance and applications (by using certificates for instance) allows to ensure that the data is indeed coming from the source it seems to come from. | Cyber Barriers | External attacker | Cyber | Manipulation | Early warning system for safe water reuse | Sewers or wastewater treatment plant | Health issues
|  |  |  | Internal attacker |  | Manipulation of the data | Web server | Csos data quality | Quantity
|  |  |  | External supplier |  |  | Sensors | Sewer system | Quality
[7 empty] | Web application | Irrigation water | False information
[7 empty] | Alert system | Digital solution users | Financial
[7 empty] | Serious game | Raw water bodies | Damage to stakeholder activtiy
[7 empty] | Web platorm (berlin) |  | Reputation
[7 empty] | Temperature sensor web-platform |  | Information leak
Ds11 flow forecast
Early warning system for bathing water quality
Ml based early warning system for bathing water
Match-making tool
Temperature sensor web-platform
Server
M68 | Access Control | Ensuring that only authorized users have access to specified resources. Can be both physical (fences, locked doors, …) and cyber. | Physical Barriers | External attacker | Cyber | Manipulation | Well-diary | Sewers or wastewater treatment plant | Health issues
|  |  | Cyber Barriers | Internal attacker |  | Manipulation of the data | Early warning system for safe water reuse | Operator | Quantity
|  |  |  | External supplier |  | Eavesdropping | Web applicaton | Csos data quality | Quality
|  |  |  | Human fault |  | Denial of service | Web server | Irrigation water | False information
[7 empty] | Sensors | Digital solution users | Financial
[7 empty] | Web application | Raw water bodies | Damage to stakeholder activtiy
[7 empty] | Alert system |  | Reputation
[7 empty] | Serious game |  | Information leak
Temperature sensor web-platform
Mobile apps to communicate bathing water quality
Ds11 flow forecast
Early warning system for bathing water quality
Ml based early warning system for bathing water
Match-making tool
Server
M69 | Jammer Detector | Specific measure for detecting the presence of a jammer device that prevents wireless communication. | Cyber Barriers | External attacker | Cyber | Denial of service | Sensors | Sewers or wastewater treatment plant | Quality
[7 empty] | Temperature sensor web-platform | Irrigation water | Financial
[7 empty] | Alert system | Csos data quality
[7 empty] | Early warning system for safe water reuse | Raw water bodies
M70 | Setting up Web Application Firewall (WAF) | Setting up a Web Application Firewal (WAF) helps protecting against different attacks such as Cross Site Scripting (XSS), SQL injection or cookie poisining for instance. Having a WAF in front of web applications can help with common and auomated attacks. | Cyber Barriers | External attacker | Cyber | Manipulation of the data | Serious game | Digital solution users | Health issues
[6 empty] | Denial of service | Web applicaton |  | False information
[7 empty] | Mobile apps to communicate bathing water quality |  | Reputation
Web server
M71 | Server side monitoring of the sensors | Sensors can be monitored from the server, for instance by sending a heartbeat. This ensures that the sensor is not physically tampered with. In addition, GPS data can be monitored to also ensure that the sensor is at the right position. | Cyber Barriers | External attacker | Cyber | Denial of service | Sensors | Sewers or wastewater treatment plant | Quality
[7 empty] | Alert system | Irrigation water
[7 empty] | Early warning system for safe water reuse | Raw water bodies
M72 | Proper device management | Device management means having the ability to enroll devices but also to revoke their access to the system (for instance in case one sensor gets stolen). Being able to update the firmware and apply secruity patches is also part of the device management. | Cyber Barriers | External attacker | Cyber | Manipulation of the data | Sensors | Digital solution users | Quality
|  |  | Consequence Mitigation |  |  |  | Alert system | Sewers or wastewater treatment plant | False information
[7 empty] | Match-making tool | Raw water bodies | Information leak
Quantity
M73 | Software security assessment | Performing software security assessment allows to discover security vulnerabilities before they are found and exploited by attackers. | Cyber Barriers | Internal attacker | Cyber | Denial of service | Serious game | Digital solution users | Reputation
Web server
M74
M75
M76
M77
M78
M79
M80
M81
M82
M83
M84
M85
M86
M87
M88
M89
M90
M91
M92
M93
M94
M95
M96
M97
M98
M99
M100
M101
M102
M103
M104
M105
M106
M107
M108
M109
M110
M111
M112
M113
M114
M115
M116
M117
M118
M119
M120
M121
M122
M123
M124
M125
M126
M127
M128
M129
M130
M131
M132
M133
M134
M135
M136
M137
M138
M139
M140
M141
M142
M143
M144
M145
M146
M147
M148
M149
M150
M151
M152
M153
M154
M155
M156
M157
M158
M159
M160
M161
M162
M163
M164
M165
M166
M167
M168
M169
M170
M171
M172
M173
M174
M175
M176
M177
M178
M179
M180
M181
M182
M183
M184
M185
M186
M187
M188
M189
M190
M191
M192
M193
M194
M195
M196
M197
M198
M199
M200
M201
M202
M203
M204
M205
M206
M207
M208
M209
M210
M211
M212
M213
M214
M215
M216
M217
M218
M219
M220
M221
M222
M223
M224
M225
M226
M227
M228
M229
M230
M231
M232
M233
M234
M235
M236
M237
M238
M239
M240
M241
M242
M243
M244
M245
M246
M247
M248
M249
M250
M251
M252
M253
M254
M255
M256
M257
M258
M259
M260
M261
M262
M263
M264
M265
M266
M267
M268
M269
M270
M271
M272
M273
M274
M275
M276
M277
M278
M279
M280
M281
M282
M283
M284
M285
M286
M287
M288
M289
M290
M291
M292
M293
M294
M295
M296
M297
M298
M299
M300
M301
M302
M303
M304
M305
M306
M307
M308
M309
M310
M311
M312
M313
M314
M315
M316
M317
M318
M319
M320
M321
M322
M323
M324
M325
M326
M327
M328
M329
M330
M331
M332
M333
M334
M335
M336
M337
M338
M339
M340
M341
M342
M343
M344
M345
M346
M347
M348
M349
M350
M351
M352
M353
M354
M355
M356
M357
M358
M359
M360
M361
M362
M363
M364
M365
M366
M367
M368
M369
M370
M371
M372
M373
M374
M375
M376
M377
M378
M379
M380
M381
M382
M383
M384
M385
M386
M387
M388
M389
M390
M391
M392
M393
M394
M395
M396
M397
M398
M399
M400
M401
M402
M403
M404
M405
M406
M407
M408
M409
M410
M411
M412
M413
M414
M415
M416
M417
M418
M419
M420
M421
M422
M423
M424
Note on C1634: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: CHECK: Can it also locate the jammer?
Note on D1707: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: if we consider the consequence of a sensor being stolen

## Options Lists
Type of Measure | Type of Source | Type of Threat | Type of Event | Specific Asset | Type of Asset | Consequence | Characteristics of Action | Risk Reduction Mechanism
Physical Barriers | External attacker | Cyber | Destruction | Additives | Catchment Area | Quantity | Proactive | Frequency/Likelihood
Cyber Barriers | Internal attacker | Physical | Interruption | Control Center | Drinking Water Network | Quality | Reactive | Consequences
Redundancy | Human fault | Cyber-Physical | Manipulation | Control System | Drinking Water Tanks | Financial | Proactive & Reactive | Frequency/Likelihood & Consequences
Control System | Natural phenomena |  | Pollution | Dosing System | Pressure Boosting Station | Reputation
Consequence Mitigation | External supplier |  |  | Drinking Water Pipes | Raw Water Bodies
Economic Policy | Interdependent CI |  |  | Drinking Water Tanks | Raw Water Pipeline
Action and Crisis Management Plans and Training |  |  |  | Drinking Water Taps | Water Abstraction Points
|  |  |  | Fire Hydrants | Water Treatment Plants
Groundwater
Media Channels
Power Transformer
Pressure Boosting Station
Pump
Sensor
Server
Spring Water
Surface Water
Transferred Information
Transmission Devices
Transmission Pipes and Equipment
Treatment Unit Process
Valve
Water under treatment
Well