## Description
Digital Water City project
Cybersecurity CoP
Risk Identification Database (RIDB)
Field | Description
Event ID | Unique numeric identifier
Type of source | Element which alone or in combination has the intrinsic potential to give rise to risk
Type of threat | The type/nature of the threat that within the DWC context could be cyber, physical or cyber-physical.
Type of event | The nature of the event
Supporting asset | The specific element (physical or virtual) where the risk source or exposure to it occurs
Composite supporting asset | The DWC solution where the risk source or exposure to it occurs, composed of supporting assets
Primary asset | Infrastructure of the water cycle where the risk event occurs
Consequence | The type of impact cause by the undesired event if materialised (outcome of an event affecting objectives).
General description | A short description of the risk event (fixed sentence structure).
Suggested by | Who proposed this event (a risk manager, a water utility operator, a technology provider, an IT expert, etc…)
Comments | Any commnet (free text)
Example 1 to 6 | Further characterization of the risk event (free text).

## STOP-IT Database (hidden)
Event Id | A Type of source | B Type of threat | C Type of event | D Specific asset | E Type of asset | F Consequence | General description | Example 1 | Example 2 | Example 3 | Example 4 | Example 5 | Example 6 | Severity
1 | External attacker | physical | pollution | groundwater | raw water bodies | quality | External attacker generates a physical caused pollution of groundwater affecting raw water bodies; which might lead to a quality issue | Addition on surface or by sub-surface injection in groundwater monitoring sites | Substances are applied to the wells by addition to monitoring pipes
2 | External attacker | cyber-physical | manipulation | transmission devices | catchment area | quantity | External attacker generates a cyber-physical caused manipulation of transmission devices affecting catchment area; which might lead to a quantity issue | data transmission wires of observation wells is manipulated. Hence no data or manipulated data reaches the control center | data transmission system of wells is manipulated
3 | External attacker | cyber-physical | destruction | transmission devices | catchment area | quantity | External attacker generates a cyber-physical caused destruction of transmission devices affecting catchment area; which might lead to a quantity issue | data transmission wires of observation wells is destroyed. Hence no data reaches the control center
4 | Natural phenomena | physical | pollution | groundwater | raw water bodies | quality | Natural phenomena generates a physical caused pollution of groundwater affecting raw water bodies; which might lead to a quality issue | Flooding causes surface runoff to infiltrate into groundwater or enter the aquifer via observation wells
5 | External attacker | cyber-physical | destruction | sensors | catchment area | quantity | External attacker generates a cyber-physical caused destruction of sensors affecting catchment area; which might lead to a quantity issue | sensors installed at wells (flow meters, hydraulic head measurement) are destroyed
6 | External attacker | cyber-physical | destruction | transmission devices | catchment area | quantity | External attacker generates a cyber-physical caused destruction of transmission devices affecting catchment area; which might lead to a quantity issue | data transmission system of wells is destroyed
7 | External attacker | physical | destruction | well | catchment area | quantity | External attacker generates a physical caused destruction of well affecting catchment area; which might lead to a quantity issue | Wells are destroyed by bombs, causing comple failure of the well
8 | External attacker | cyber-physical | destruction | sensors | water treatment plant | quantity | External attacker generates a cyber-physical caused destruction of sensors affecting water treatment plant; which might lead to a quantity issue | Perpetrators enter the WTP and destroy the sensors. No data or manipulated data is reaching the control center. Thus a proper operation of the WTP cannot be guaranteed
9 | External attacker | cyber-physical | destruction | sensors | water treatment plant | quality | External attacker generates a cyber-physical caused destruction of sensors affecting water treatment plant; which might lead to a quality issue | Perpetrators enter the WTP and destroy the sensors. No data or manipulated data is reaching the control center. Thus a proper operation of the WTP cannot be guaranteed leading to a disturbed supply with clean drinking water
10 | External attacker | cyber-physical | manipulation | transmission devices | water treatment plant | quality | External attacker generates a cyber-physical caused manipulation of transmission devices affecting water treatment plant; which might lead to a quality issue | Perpetrators enter the WTP and manipulate the data transmission system. No data or manipulated data is reaching the control center. Thus a proper operation of the WTP cannot be guaranteed.
11 | External attacker | cyber-physical | destruction | transmission devices | water treatment plant | quantity | External attacker generates a cyber-physical caused destruction of transmission devices affecting water treatment plant; which might lead to a quantity issue | Perpetrators enter the WTP and destroys the data transmission wires. No data is reaching the control center. Thus a proper operation of the WTP cannot be guaranteed. | Tha data transmission system of power transformers is destroyed, therefore, no data is reaching the control center. As a result, a proper ooperation of the power transformer cannot be guaranteed, which leads to an insuficient amount of electrical energy delivered by the power transformer, making impossible to sustain treatment
12 | External attacker | cyber-physical | manipulation | dosing system | water treatment plant | quality | External attacker generates a cyber-physical caused manipulation of dosing system affecting water treatment plant; which might lead to a quality issue | Chemicals used in the drinking water treatment are dosed inadequately by manipulation of control system. Intrusion into control system and manipulation remain undetected
13 | Natural phenomena | physical | pollution | water under treatment | water treatment plant | quality | Natural phenomena generates a physical caused pollution of water under treatment affecting water treatment plant; which might lead to a quality issue | Flooding causes surface runoff to reach WTP and contaminate water being treated. Contaminated air reached WTP and contaminate water being treated
14 | Natural phenomena | physical | destruction | additives | water treatment plant | quality | Natural phenomena generates a physical caused destruction of additives affecting water treatment plant; which might lead to a quality issue | Chemicals used in the drinking water treatment are dosed inadequately as a result of a natural event which destroys the reagents dosing system. The intrusion into the building and manipulation remain undetected and the missdosage can not be corrected in the process any more | Chemicals used in the drinking water treatment are dosed inadequately as a result of a natural event which alters the reagents dosing system. The intrusion into the building and manipulation remain undetected and the missdosage can not be corrected in the process any more
15 | Human fault | physical | pollution | water under treatment | water treatment plant | quality | Human fault generates a physical caused pollution of water under treatment affecting water treatment plant; which might lead to a quality issue | Chemicals used in the drinking water treatment are dosed inadequately due to errors by the oeprational staff. The missdosage remains undetected and can not be corrected in the process any more. The missdosage has a negative impact on the drinking water quality.
16 | External attacker | physical | pollution | additives | water treatment plant | quality | External attacker generates a physical caused pollution of additives affecting water treatment plant; which might lead to a quality issue | Chemicals used in drinking water treatment are altered by adding other substances to them , changing thus their composition. The pollution of the chemicals remains undetected and the pollutant cannot be removed in the process any more.
17 | Human fault | cyber-physical | manipulation | control system | drinking water network | quantity | Human fault generates a cyber-physical caused manipulation of control system affecting drinking water network; which might lead to a quantity issue | Wrong operation of SCADA causes pressure drop below minimum allowed, causing water unavailability | Wrong operation of SCADA causes pressure rise above maximum allowed, causing pipe break | SCADA software failure due to wrong updating or malfunctioning resulting in a disturbance of the normal operating process leading to a interruption of the water supply
18 | Human fault | cyber-physical | manipulation | control system | drinking water network | quality | Human fault generates a cyber-physical caused manipulation of control system affecting drinking water network; which might lead to a quality issue | Wrong operation of SCADA causes pressure drop below minimum allowed, causing water contamination due to external water entering the pipes via leakages
19 | External attacker | physical | destruction | pressure boosting station | pressure boosting station | quantity | External attacker generates a physical caused destruction of pressure boosting station; which might lead to a quantity issue | Perpetrators damage pumps or similar (by bombs) making them unable to work properly and provide required pressure
20 | External attacker | cyber-physical | manipulation | sensors | pressure boosting station | quantity | External attacker generates a cyber-physical caused manipulation of sensors affecting pressure boosting station; which might lead to a quantity issue | pepetrators enter the pressure boosting station, manipulating flow meters, pressure sensors… A proper operation of the PBS cannot be guaranteed
21 | External attacker | cyber-physical | destruction | sensors | pressure boosting station | quantity | External attacker generates a cyber-physical caused destruction of sensors affecting pressure boosting station; which might lead to a quantity issue | pepetrators enter the pressure boosting station, manipulating flow meters, pressure sensors… A proper operation of the PBS cannot be guaranteed
22 | External attacker | cyber-physical | manipulation | transmission devices | pressure boosting station | quantity | External attacker generates a cyber-physical caused manipulation of transmission devices affecting pressure boosting station; which might lead to a quantity issue | pepetrators enter the pressure boosting station, manipulating data transmission system… A proper operation of the PBS cannot be guaranteed | Manipulation of data transmission: Manipulated data is reaching the control center thus a proper ooperation of the pressure boosting station cannot be guaranteed. This leads to an insuficient amount of electrical energy delivered by the power transformer, making impossible to sustain distribution processes
23 | External attacker | cyber-physical | destruction | transmission devices | pressure boosting station | quantity | External attacker generates a cyber-physical caused destruction of transmission devices affecting pressure boosting station; which might lead to a quantity issue | pepetrators enter the pressure boosting station, manipulating data transmission system… A proper operation of the PBS cannot be guaranteed
24 | Human fault | physical | manipulation | drinking water pipes | drinking water network | quality | Human fault generates a physical caused manipulation of drinking water pipes affecting drinking water network; which might lead to a quality issue | Wrong installation; connecting drinking water pipes to non-drinking water pipes, leading to contamination of the drinking water
25 | External attacker | physical | pollution | drinking water taps | drinking water network | quality | External attacker generates a physical caused pollution of drinking water taps affecting drinking water network; which might lead to a quality issue | Substances are introduced to DWN via pumping them through taps. Contamination remains undetected and spreads in direction of flow in the network
26 | External attacker | physical | pollution | fire hydrants | drinking water network | quality | External attacker generates a physical caused pollution of fire hydrants affecting drinking water network; which might lead to a quality issue | Substances are introduced to DWN via pumping them through fire hydrants. Contamination remains undetected and spreads in direction of flow in the network
27 | External attacker | physical | destruction | drinking water pipes | drinking water network | quantity | External attacker generates a physical caused destruction of drinking water pipes affecting drinking water network; which might lead to a quantity issue | Destruction of parts of the network
28 | External attacker | physical | pollution | drinking water tanks | drinking water tanks | quality | External attacker generates a physical caused pollution of drinking water tanks; which might lead to a quality issue | Biological, chemical or radioactive substances are pumped into the storage tank
29 | External attacker | cyber-physical | manipulation | sensors | drinking water tanks | quantity | External attacker generates a cyber-physical caused manipulation of sensors affecting drinking water tanks; which might lead to a quantity issue | Fake signals are sent to the control center due to a cyber manipulation of the sensor. This leads to an unintended emptying or overflow of the storage tank based on wrong information | measurements from sensors are supressed causing undetected overflow or drainage of storage tanks | In-situ manipulation of the sensors leading to false information being sent to the control center. This leads to an unintended emptying or overflow of the storage tank based on wrong information | In-situ manipulation of water level meter, sending false signals, leading to water tanks being emptied
30 | External attacker | cyber-physical | manipulation | transmission devices | drinking water tanks | quantity | External attacker generates a cyber-physical caused manipulation of transmission devices affecting drinking water tanks; which might lead to a quantity issue | In-situ manipulation of data transmission system leading to false information being sent to the control center. This leads to an unintended emptying or overflow of the storage tank based on wrong information
31 | External attacker | physical | destruction | drinking water tanks | drinking water tanks | quantity | External attacker generates a physical caused destruction of drinking water tanks; which might lead to a quantity issue | Physical attacks such as by bombing can cause extreme damage to water tanks
32 | External attacker | cyber-physical | manipulation | control system | pressure boosting station | quantity | External attacker generates a cyber-physical caused manipulation of control system affecting pressure boosting station; which might lead to a quantity issue | Due to a direct cyber attack on pumps their settings are changed or they are switched off. Thus the flow and the pressure in the water network cannot be maintained | Manipulation of control devices in pumping station (Pump station indicate normal operation, but operator is exposed to wrong measurements of pressure, level, flow while pumps are malfunctioning), leading to pumping station failure (with high MTTR) leading to unavailability of water for distribution. | Received incorrect data in the control center causing operators misjudgment of the system performance. As a result, over pumping is performed leading to electricity overcharge and GHE. | Attacker get access to remote site and changes made to the PLCs software. As a result, pumps are operated at higher speed than they are designed for causing overheating and malfunctioning thus putting in risk the water suppky.
33 | Interdependent CI | physical | interruption | power transformer | water treatment plant | quantity | Interdependent CI generates a physical caused interruption of power transformer affecting water treatment plant; which might lead to a quantity issue | Due to loss of external power supply the treatment process cannot be sustained
34 | Interdependent CI | physical | interruption | power transformer | pressure boosting station | quantity | Interdependent CI generates a physical caused interruption of power transformer affecting pressure boosting station; which might lead to a quantity issue | Due to loss of external power supply the water supply cannot be sustained
35 | External attacker | cyber-physical | destruction | transmission devices | pressure boosting station | quantity | External attacker generates a cyber-physical caused destruction of transmission devices affecting pressure boosting station; which might lead to a quantity issue | No data is reaching the control center thus a proper ooperation of the pressure boosting station cannot be guaranteed. This leads to an insuficient amount of electrical energy delivered by the power transformer, making impossible to sustain distribution processes | Perpetrators enter the WTP and destroy the data transmission wires. No data is reaching the control center. Thus a proper operation of the WTP cannot be guaranteed.
36 | External attacker | physical | destruction | power transformer | water treatment plant | quantity | External attacker generates a physical caused destruction of power transformer affecting water treatment plant; which might lead to a quantity issue | Destruction of the power transformer caused by a malicious human act (sabotage), causing mafunction of the treatment process.
37 | External attacker | physical | destruction | power transformer | pressure boosting station | quantity | External attacker generates a physical caused destruction of power transformer affecting pressure boosting station; which might lead to a quantity issue
38 | External attacker | cyber-physical | manipulation | sensors | water treatment plant | quantity | External attacker generates a cyber-physical caused manipulation of sensors affecting water treatment plant; which might lead to a quantity issue | The operator does not see what is happening and does not receive alarms while control is shutting down. Causing failure of control system | Perpetrators enter the WTP and manipulate the sensors. No data or manipulated data is reaching the control center. Thus a proper operation of the WTP cannot be guaranteed
39 | External attacker | cyber-physical | manipulation | sensors | water treatment plant | quality | External attacker generates a cyber-physical caused manipulation of sensors affecting water treatment plant; which might lead to a quality issue | The operator does not see what is happening and does not receive alarms while control is shutting down. Causing failure of control system | Manipulation of sensors in water treatment plants. Perpetrators enter the WTP and manipulate the sensors. No data or manipulated data is reaching the control center. Thus a proper operation of the WTP cannot be guaranteed leading to a disturbed supply with clean drinking water
40 | External attacker | cyber-physical | manipulation | control system | water treatment plant | quantity | External attacker generates a cyber-physical caused manipulation of control system affecting water treatment plant; which might lead to a quantity issue | Raw water pumps and alternative pumps are shut down by hacking and the operator does not see what is happenign | Malicious crafted commands are sent to control system of pumps causing them to malfunction | Alarms from remote equipment at the plant are supressed, making it impossible to detect errors and resulting in unavailability of drinking water from treatment plant
41 | External attacker | cyber-physical | manipulation | sensors | catchment area | quantity | External attacker generates a cyber-physical caused manipulation of sensors affecting catchment area; which might lead to a quantity issue | Control devices sending false water level measurements from sensors, leading to inappropriate management of reservoir | sensors installed at wells (flow meters, hydraulic head measurement) are manipulated
42 | External attacker | cyber-physical | manipulation | transmission devices | water treatment plant | quantity | External attacker generates a cyber-physical caused manipulation of transmission devices affecting water treatment plant; which might lead to a quantity issue | Remote network equipment is compromised, causing a denial of service for all network communications between central control system and WTP, leaving the WTP not supervised until it can be reached physically by operators AND the cleanwater reservoirs are low | Perpetrators enter the WTP and manipulates the data transmission system. No data or manipulated data is reaching the control center. Thus a proper operation of the WTP cannot be guaranteed. | Tha data transmission system of power transformers is manipulated, therefore, fake data is reaching the control center. As a result, proper operation of the power transformer cannot be guaranteed, which leads to an insuficient amount of electrical energy delivered by the power transformer, making impossible to sustain treatment
43 | External attacker | cyber-physical | manipulation | control system | catchment area | quantity | External attacker generates a cyber-physical caused manipulation of control system affecting catchment area; which might lead to a quantity issue | denial of service is caused against remote equipment in charge of dam gates, making remotre control not possible and leading to possible downstream flooding, risking damage to property, persons and environment
44 | External attacker | cyber-physical | manipulation | control system | water treatment plant | quality | External attacker generates a cyber-physical caused manipulation of control system affecting water treatment plant; which might lead to a quality issue | failure in hygienic barriers caused by loss of control system due to manipulation, resulting in microbiological contamination at the water supply network in presence of heavy rain and extreme micro-organism load. This results to microbial contamination of drinking water | Malicious software on the PLC (no backup system). Temporary disruption of treatment | Damage to the operational control system and disabling the disinfection and monitoring systems
45 | External attacker | cyber-physical | manipulation | control system | wastewater treatment plant | quality | External attacker generates a cyber-physical caused manipulation of control system affecting wastewater treatment plant; which might lead to a quality issue | Failure control system at the outflow to recipients caused by the loss of control system . This will lead to WWTP failure which will result to failure at sanitation system leading to source-surface water microbial contamination | Exceeded hydraulic capacity and overflow to recipients caused by the loss of control system resulting to WWTP failure which will result to failure at sanitation system leading to source-surface water microbial contamination | Failed control system at the outflow to recipients caused by the loss of control system. This will lead to WWTP failure which will result to failure at sanitation system leading to source-surface water chemical contamination | Exceeded hydraulic capacity and overflow to recipients caused by the loss of control system will lead to failure at sanitation system leading to source-surface water chemical contamination
46 | Human fault | physical | manipulation | valve | drinking water network | quantity | Human fault generates a physical caused manipulation of valve affecting drinking water network; which might lead to a quantity issue | Valve failure due to wrong operation or malfunction
47 | External attacker | cyber-physical | destruction | control center | drinking water network | quantity | External attacker generates a cyber-physical caused destruction of control center affecting drinking water network; which might lead to a quantity issue | Control center is destroyed due to intentional fire | Control center is destroyed due to intentional flood resulting in impossibility to operate the network and subsequently interruption of water supply for extended period.
48 | Human fault | cyber-physical | destruction | control center | drinking water network | quantity | Human fault generates a cyber-physical caused destruction of control center affecting drinking water network; which might lead to a quantity issue | Control center is destroyed due to accidental fire | Control center is destroyed due to accidental flood resulting in impossibility to operate the network and subsequently interruption of water supply for extended period.
49 | External attacker | cyber-physical | manipulation | control system | drinking water network | quality | External attacker generates a cyber-physical caused manipulation of control system affecting drinking water network; which might lead to a quality issue | An intruder accesses a restricted area due to failure in the authorization procedure, and causes disturbances in water supply, leading to higher reagent dose than needed, which would result in water contamination | Intruder damages the water supply system by operating outside specifications, e.g. overdosing. Result is long term inavailability of the system and backup facilities simultaniously failing.
50 | External attacker | cyber | manipulation | server | - | financial | External attacker generates a cyber caused manipulation of server; which might lead to a financial issue | A hacker get access to the water utility server and leaks confidential information of the the organization and the customers | A hacker gets access to water utility server and manipulates technical data as well as spreading private data of the Water Company. The hacker shows the security vulnerabilities of the company | A file with malicious code (e.g. Excel VBA macros) enters the company's network by email and infecting the network and computers with hostile software. Financial records are deleted and payments to suppliers are delayed causing repair parts shortage and pipe fixes deferred. | Hacker breaks into GIS data system and corrupts the data so that correct location of pipes and valves is no longer known
51 | Internal attacker | cyber | manipulation | server | - | financial | Internal attacker generates a cyber caused manipulation of server; which might lead to a financial issue | Frustrated employee leaked infrastructure assets sensitive informant leading to increased vulnerability of company's sites. | Recruitment of employees with access to computers, without security checks causing leaks of sensitive information encouraging terrorist attacks plans.
52 | External attacker | cyber | manipulation | transferred information | pressure boosting station | quantity | External attacker generates a cyber caused manipulation of transferred information affecting pressure boosting station; which might lead to a quantity issue | Communication jamming to remote sites leading to pumps malfunctioning causing water supply shortage and pressure reduction.
53 | External attacker | cyber | manipulation | transferred information | drinking water network | quality | External attacker generates a cyber caused manipulation of transferred information affecting drinking water network; which might lead to a quality issue | Internet penetration to the operational communications network, blocking communication to remote site causing changes to additive optimal dosing. | Disturbance of radio signal communication to systems or sensors
54 | External attacker | cyber-physical | destruction | control system | pressure boosting station | quantity | External attacker generates a cyber-physical caused destruction of control system affecting pressure boosting station; which might lead to a quantity issue | Damage of a local controller at remote site unabling the operators to control the pumps and to supply water.
55 | External attacker | cyber-physical | destruction | control system | drinking water network | quality | External attacker generates a cyber-physical caused destruction of control system affecting drinking water network; which might lead to a quality issue | An attacker physically damages the control system at the water source causing disinfection dosing modification. As a result, at the water consumers taps THMs are formed.
56 | External attacker | physical | destruction | dosing system | drinking water network | quality | External attacker generates a physical caused destruction of dosing system affecting drinking water network; which might lead to a quality issue | An attacker physically damages the water disinfection system at the water source causing disinfection dosing modification. As a result, at the water consumers taps THMs are formed.
57 | External attacker | cyber-physical | manipulation | control system | drinking water tanks | reputation | External attacker generates a cyber-physical caused manipulation of control system affecting drinking water tanks; which might lead to a reputation issue | Cyber remote manipulation of PLCs data to send copied information to the SCADA system "blinding" the operator not to see the real situation in the network cuasing tanks to overflow and flood private property.
58 | Human fault | cyber-physical | manipulation | control system | drinking water tanks | reputation | Human fault generates a cyber-physical caused manipulation of control system affecting drinking water tanks; which might lead to a reputation issue | Human error in updating operating system caused deactivating the SCADA server leading to false positive alarms from Event Detection System causing water sampling teams to be unnecessarily deployed.
59 | External supplier | cyber-physical | manipulation | control system | drinking water network | quantity | External supplier generates a cyber-physical caused manipulation of control system affecting drinking water network; which might lead to a quantity issue | Subcontractor physically disconnecting the local PLC. As a result, the PLC transmission is disturbed causing a wrong image of the local situation of the system. Consequently, the PRV at the downstream pipe malfunctions to supply high pressure and increase leaks.
60 | External attacker | cyber-physical | manipulation | sensors | drinking water network | reputation | External attacker generates a cyber-physical caused manipulation of sensors affecting drinking water network; which might lead to a reputation issue | Hacker gets control of sensors and generate water quality false alarms causing the closure of water pipes and issuing a "do not drink" public message. | The signal from one or multiple sensors is manipulated to give a false alarm of contamination, leading to social disruption (unnecessary public warnings, boil water notice)
61 | External attacker | physical | pollution | drinking water pipes | drinking water network | quality | External attacker generates a physical caused pollution of drinking water pipes affecting drinking water network; which might lead to a quality issue | Contaminated water at the tap, due to a contaminant dosed in the distribution system
62 | External attacker | cyber-physical | manipulation | sensors | drinking water network | quality | External attacker generates a cyber-physical caused manipulation of sensors affecting drinking water network; which might lead to a quality issue | Contaminated water at the tap, due to blocking/faking of signals from sensors
63 | Interdependent CI | physical | pollution | surface water | raw water bodies |  | Interdependent CI generates a physical caused pollution of surface water affecting raw water bodies; which might lead to a issue | Industries in the catchment are attacked leading to large, serious spills in the river water and a very long intake stop.
64 | External attacker | physical | manipulation | valve | water treatment plant | quantity | External attacker generates a physical caused manipulation of valve affecting water treatment plant; which might lead to a quantity issue | A valve is opened which causes flooding of equipment, e.g. pumping celler causing long term unavailability
65 | External attacker | cyber-physical | manipulation | control system | raw water bodies | quantity | External attacker generates a cyber-physical caused manipulation of control system affecting raw water bodies; which might lead to a quantity issue | The surface water system management is attacked (external party e.g. water board) leading to mismanagement of the suface water system and consequently water shortage at intake of WTP.
66 | External attacker | physical | manipulation | pump | drinking water network | quantity | External attacker generates a physical caused manipulation of pump affecting drinking water network; which might lead to a quantity issue | Increasing pumping pressure to cause break
67 | External attacker | physical | manipulation | valve | drinking water network | quantity | External attacker generates a physical caused manipulation of valve affecting drinking water network; which might lead to a quantity issue | Create water hammer by shutting valve causing water hammer | An intruder accesses a restricted area due to failure in the authorization procedure, and causes disturbances in water supply, leading to pipe burst and/or interruption of water supply.
68 | External attacker | physical | manipulation | drinking water pipes | drinking water network | quantity | External attacker generates a physical caused manipulation of drinking water pipes affecting drinking water network; which might lead to a quantity issue | Cathode corrosion stolen/destroyed/manipulated leading to increased corrosion of pipes and thus increase of pipe breaks
69 | External attacker | cyber-physical | manipulation | control system | drinking water network | quantity | External attacker generates a cyber-physical caused manipulation of control system affecting drinking water network; which might lead to a quantity issue | Disrupting distribution control, thus depleting daily capacity (wells, treatment) | attacker utilizes the logical communication path towards remote equipment to override PLC logic and change ladder logic leading to malfunctioning of the control system in the remote station or wrong measurements being returned to the SCADA system | Takeover of the control of the process by an external cyber attack. This leads to manipulation of settings in the supply chain like the stopping of pumps, closing of valves (water hammers) or similar. In some cases this can cause physical destruction of parts of the network | pumps and valves are manipulated through scada commands to create a hammerefect inducing wear and tear on pipes and eventually pipe breaks | Intruder damages the water supply system by operating outside specifications, e.g. increasing pressure leading to pipe breaks, opening valves leading to flooding. Result is long term inavailability of the system and backup facilities simultaniously failing. | Wrong operation during repair&maintenance caused by the loss of system control (and insufficient compensation at utility's storage tanks), resulting to relevant water losses from major pipe breaks
70 | External attacker | cyber | manipulation | server | - | quality | External attacker generates a cyber caused manipulation of server; which might lead to a quality issue | The water consumption prediction is corrupted and therefore reservoirs are empty during the evening peak demand, leading to loss of pressure and consequently Microbiological contamination at the tap leading to health risk | The threat agent gains unauthorized access to information assets in transit (i.e. ‘sniffing’), and potentially alters information while it is being transmitted. | The threat agent introduces malware to an organisation’s information systems. | The threat agent exploits misconfigured information systems (i.e. those not configured in accordance with security standards, or organisational build requirements) in order to gain unauthorised access.
71 | External attacker | cyber | manipulation | transferred information | drinking water network | quantity | External attacker generates a cyber caused manipulation of transferred information affecting drinking water network; which might lead to a quantity issue | Disturbance of radio signal communication to systems or sensors
72 | External attacker | cyber | manipulation | media channels | - | reputation | External attacker generates a cyber caused manipulation of media channels; which might lead to a reputation issue | Manipulation of public communication of water company (not a physical effect, but could be combined with a physical consequense to increase the impact)
73 | External attacker | cyber-physical | manipulation | control system | drinking water tanks | quantity | External attacker generates a cyber-physical caused manipulation of control system affecting drinking water tanks; which might lead to a quantity issue | Manipulation (hacking) of PLC handling the measurements before they are tranferred to SCADA system, leading to water tanks being emptied leading to water loss and water supply failure and unavailability of water for distribution.
74 | External attacker | cyber | manipulation | server | - | quantity | External attacker generates a cyber caused manipulation of server; which might lead to a quantity issue | The threat agent obtains unauthorized control of (hijacks) a pre-existing, legitimate network session between information systems, or between information systems and end users. | The threat agent gains unauthorized access to information assets in transit (i.e. ‘sniffing’), and potentially alters information while it is being transmitted. | The threat agent introduces malware to an organisation’s information systems. | The threat agent exploits misconfigured information systems (i.e. those not configured in accordance with security standards, or organisational build requirements) in order to gain unauthorised access.
75 | External attacker | cyber | manipulation | server | - | reputation | External attacker generates a cyber caused manipulation of server; which might lead to a reputation issue | The threat agent obtains unauthorized access to legitimate authentication credentials, and uses these to gain access to an organization’s information systems. | The threat agent exploits vulnerabilities in the authorization mechanisms of an organization’s information systems in order to gain access to sensitive functions and information assets. | The threat agent obtains organizational information assets due to insecure disposal. | The threat agent obtains physical access to an organisation's information systems (e.g. by misusing access or bypassing physical security checks) and uses this access to gain unauthorised access to organisational information systems and information assets.
76 | Human fault | cyber | manipulation | server | - | reputation | Human fault generates a cyber caused manipulation of server; which might lead to a reputation issue | Accidental errors made by an authorized user (internal or external) when using or maintaining information systems.
77 | Human fault | cyber | manipulation | server | - | quantity | Human fault generates a cyber caused manipulation of server; which might lead to a quantity issue | Incorrect execution or failure of software acquired from an external party (e.g. enterprise applications and commercial-off-the-shelf (COTS) software (such as ERP, CRM), office productivity software, communications software and security software).
78 | Human fault | cyber | manipulation | server | - | quality | Human fault generates a cyber caused manipulation of server; which might lead to a quality issue | Incorrect execution or failure of software acquired from an external party (e.g. enterprise applications and commercial-off-the-shelf (COTS) software (such as ERP, CRM), office productivity software, communications software and security software).
79 | Human fault | cyber-physical | manipulation | server | - | quantity | Human fault generates a cyber-physical caused manipulation of server; which might lead to a quantity issue | Failure to regulate the temperature, humidity and air quality in environments where information systems are located (e.g. data centres)
80 | Human fault | cyber-physical | manipulation | server | - | quality | Human fault generates a cyber-physical caused manipulation of server; which might lead to a quality issue | Failure to regulate the temperature, humidity and air quality in environments where information systems are located (e.g. data centres)
81 | Interdependent CI | physical | pollution | water under treatment | water treatment plant | quality | Interdependent CI generates a physical caused pollution of water under treatment affecting water treatment plant; which might lead to a quality issue | Contaminated air reaches WTP and contaminates water being treated

## STOP-IT Options (hidden)
Type of source | Type of threat | Type of event | Specific asset | Type of Asset | Consequence dimension
External attacker | Cyber | Destruction | Additives | Catchment area | Financial
External supplier | Cyber-physical | Interruption | Control center | Drinking water network | Quality
Human fault | Physical | Manipulation | Control system | Drinking water tanks | Quantity
Interdependent CI |  | Pollution | Dosing system | Pressure boosting station | Reputation
Internal attacker |  |  | Drinking water pipes | Raw water bodies
Natural phenomena |  |  | Drinking water tanks | Wastewater treatment plant
|  |  | Drinkinkg water taps | Water abstraction points
|  |  | Fire hydrants | Water treatment plants
Groundwater
Media channels
Power transformer
Pressure boosting station
Pump
Sensor
Server
Spring water
Surface water
Transferred information
Transmission devices
Valve
Water under treatment
Well
NB: It is not the intention of this table to provide an exact severity scale but to provide a set of orientative values and qualitative descriptions. It is essential that the table is adjusted to each company's reality.
| Severity | Negligible | Minor | Moderate | Major | Extreme
|  | 1 | 2 | 3 | 4 | 5
| Economic loss | < 5k € | < 50k € | < 500k € | < 5M € | > 5M €
| Health impact | No health impact | Few people with mild injuries | Many people with mild injuries. Some with chronic deseases | Few deaths | Many deaths
| Interruption of service | < 100 | < 1000 | < 10.000 | < 100.000 | > 1.000.000
| Disruption of other services (cascading effects) |  |  |  | > 1 service affected | > 2 services affected
| Reputation | Rumours, no media coverage | Local media coverage - short term | Long-term adverse publicity in local media. Significant effect on public perception of the organization | National media less than 4 days | National/international media more than 4 days

## DWC - Database
Event Id | A Type of source | B Type of threat | C Type of event | D Supporting asset | E Composite asset | F Primary asset | G Consequence | General description | suggested by | comments | Example 1 | Measures |  | Example 5 | Example 6 | Severity
1 | External Attacker | Physical | Discharge of pollutants | Sensors | ALERT SYSTEM | Raw water bodies | Quality | External Attacker generates a Physical threat causing a Discharge of pollutants of the Sensors of the ALERT SYSTEM which affects Raw water bodies and might lead to a Quality issue | SIAAP |  | An attacker discharge pollutants near a sensor tricking the measurement into issuing a warning; leading to quality issues of the bathing water. | 11, 26, 27, 28, 29, 30
2 | External Attacker | cyber | Denial of Service | Sensors | ALERT SYSTEM | Raw water bodies | Quality | External Attacker generates a cyber threat causing a Denial of Service of the Sensors of the ALERT SYSTEM which affects Raw water bodies and might lead to a Quality issue | SINTEF |  | An attacker who knows where are the different sensors put small jammers close to them, preventing them to connect. | 30, 69, 71
3 | External Attacker | cyber | Denial of Service | Sensors | ALERT SYSTEM | Sewers or Wastewater treatment plant | Quality | External Attacker generates a cyber threat causing a Denial of Service of the Sensors of the ALERT SYSTEM which affects Sewers or Wastewater treatment plant and might lead to a Quality issue | SINTEF |  | An attacker who knows where are the different sensors put small jammers close to them, preventing them to connect. | 30, 69, 71
4 | External Attacker | cyber | Manipulation of the data | Sensors | ALERT SYSTEM | Sewers or Wastewater treatment plant | Quality | External Attacker generates a cyber threat causing a Manipulation of the data of the Sensors of the ALERT SYSTEM which affects Sewers or Wastewater treatment plant and might lead to a Quality issue | SINTEF |  | An attacker steal a sensor in order to access the firmware on it an possibly get access to the server (he might want to send fake data). | 46, 48, 54, 67, 68, 72
5 | External Attacker | cyber | Manipulation of the data | Sensors | ALERT SYSTEM | Raw water bodies | Quality | External Attacker generates a cyber threat causing a Manipulation of the data of the Sensors of the ALERT SYSTEM which affects Raw water bodies and might lead to a Quality issue | SINTEF |  | An attacker steal a sensor in order to access the firmware on it an possibly get access to the server (he might want to send fake data). | 46, 48, 54, 67, 68, 72
6 | External Attacker | cyber | Manipulation of the data | Sensors | ALERT SYSTEM | Raw water bodies | Information leak | External Attacker generates a cyber threat causing a Manipulation of the data of the Sensors of the ALERT SYSTEM which affects Raw water bodies and might lead to a Information leak issue | SINTEF |  | An attacker steal a sensor in order to access the firmware on it an possibly get access to the server (he might want to send fake data). | 46, 48, 54, 67, 68, 72
7 | External Attacker | cyber | Manipulation of the data | Sensors | ALERT SYSTEM | Raw water bodies | False information | External Attacker generates a cyber threat causing a Manipulation of the data of the Sensors of the ALERT SYSTEM which affects Raw water bodies and might lead to a False information issue | SINTEF |  | An attacker steal a sensor in order to access the firmware on it an possibly get access to the server (he might want to send fake data). | 46, 48, 54, 67, 68, 72
8 | External Attacker | cyber | Manipulation of the data | Server | ALERT SYSTEM | Raw water bodies | Information leak | External Attacker generates a cyber threat causing a Manipulation of the data of the Server of the ALERT SYSTEM which affects Raw water bodies and might lead to a Information leak issue | SINTEF | revised by SIAAP | An attacker hacks into the platform controlling the ALERT system and gets access to the database | 26, 27, 28, 29, 46, 48, 54, 67, 68
9 | External Attacker | cyber | Manipulation of the data | Server | ALERT SYSTEM | Raw water bodies | False information | External Attacker generates a cyber threat causing a Manipulation of the data of the Server of the ALERT SYSTEM which affects Raw water bodies and might lead to a False information issue | SINTEF | revised by SIAAP | An attacker hacks into the platform controlling the ALERT system and changes the data | 26, 27, 28, 29, 46, 48, 54, 67, 68
10 | External Attacker | cyber | Denial of Service | Server | ALERT SYSTEM | Raw water bodies | Quality | External Attacker generates a cyber threat causing a Denial of Service of the Server of the ALERT SYSTEM which affects Raw water bodies and might lead to a Quality issue | SINTEF | revised by SIAAP | An attacker hacks into the platform controlling the ALERT system and prevent it from sampling. | 30, 58, 66
11 | Human fault | cyber | Denial of service | Server | DS 12 Decision support system | Sewers or Wastewater treatment plant | Reputation | Human fault generates a cyber threat causing a Denial of service of the Server of the DS 12 Decision support system which affects Sewers or Wastewater treatment plant and might lead to a Reputation issue | BIOFOS | revised by BIOFOS | System changes in the internal network setup causes several servers and therefore the decission support system to be offline and unavailable. | 30, 58, 66 | 30: RedundantAssetsAndInfrastructures 58: NetworkTrafficAnalysis 66: DDoS Protection
12 | Internal attacker | cyber | Denial of service | Server | DS 12 Decision support system | Sewers or Wastewater treatment plant | Reputation | Internal attacker generates a cyber threat causing a Denial of service of the Server of the DS 12 Decision support system which affects Sewers or Wastewater treatment plant and might lead to a Reputation issue | BIOFOS | revised by BIOFOS | An internal attacker has the opertunity to place a hardware device on the internal network causing a DDoS attack on several internal servers witch affects the availability of the Decission support system. | 30, 58, 66 | 30: RedundantAssetsAndInfrastructures 58: NetworkTrafficAnalysis 66: DDoS Protection
13 | External supplier | cyber | Denial of service | Server | DS 12 Decision support system | Sewers or Wastewater treatment plant | Reputation | External supplier generates a cyber threat causing a Denial of service of the Server of the DS 12 Decision support system which affects Sewers or Wastewater treatment plant and might lead to a Reputation issue | BIOFOS | revised by BIOFOS | An extranal supplier has lost a tender and one of the external employees places a script/program on a server that causes the Decision support system to be unavailable. | 30, 58, 66 | 30: RedundantAssetsAndInfrastructures 58: NetworkTrafficAnalysis 66: DDoS Protection
14 | Internal attacker | cyber | Spoofing | Web application | DS 13 Interface | Sewers or Wastewater treatment plant | Quantity | Internal attacker generates a cyber threat causing a Spoofing of the Web application of the DS 13 Interface which affects Sewers or Wastewater treatment plant and might lead to a Quantity issue | BIOFOS | revised by BIOFOS | An internal attacker with server access manipulates the data feed from the Decision support system to the Web application causing the Web application to show wrong / fake data to end users | 26,27,28,46, 50, 58, 60 | 26: ProcedureForPersonnelChanges 27: EmployeesTrainings 28: SecurityCheckOfEmployees 46: RestrictedAccesToITSystem 50: NetworkSeparation 58: NetworkTrafficAnalysis 60: Software Management
15 | External supplier | cyber | Spoofing | Web application | DS 13 Interface | Sewers or Wastewater treatment plant | Quality | External supplier generates a cyber threat causing a Spoofing of the Web application of the DS 13 Interface which affects Sewers or Wastewater treatment plant and might lead to a Quality issue | BIOFOS | revised by BIOFOS | An employee at a extranal supplier is fired, but before the employee access to the it systems he manages is closed the employee changes the access to the server by adding a new user with administrative server rights. | 46, 50,58,60,63 | 46: RestrictedAccesToITSystem 50: NetworkSeparation 58: NetworkTrafficAnalysis 60: Software Management 63: SecureOutsourcing
17 | External attacker | cyber | Denial of Service | Web application | DS 13 Interface | Sewers or Wastewater treatment plant | Reputation | External attacker generates a cyber threat causing a Denial of Service of the Web application of the DS 13 Interface which affects Sewers or Wastewater treatment plant and might lead to a Reputation issue | BIOFOS |  | An attacker dos the platform, making it unavailable to end users, or to the public and leading to a reputation issue. | 30, 58, 66 | 30: RedundantAssetsAndInfrastructures 58: NetworkTrafficAnalysis 66: DDoS Protection
18 | Human fault | physical | Destruction | Sensors | DS11 Flow forecast | Sewers or Wastewater treatment plant | Not serious | Human fault generates a physical threat causing a Destruction of the Sensors of the DS11 Flow forecast which affects Sewers or Wastewater treatment plant and might lead to a Not serious issue | BIOFOS |  | A flow sensor is accidentially broken and no data is received. The control software is made with fall-back in case of sensor failure. Sensor failure or no data or data flatline will trigger en alarm to a operator | 3,11,30 | 3: CameraSurveillance 11: DiscreetAppearance 30: RedundantAssetsAndInfrastructures
19 | Internal attacker | physical | Destruction | Sensors | DS11 Flow forecast | Sewers or Wastewater treatment plant | Not serious | Internal attacker generates a physical threat causing a Destruction of the Sensors of the DS11 Flow forecast which affects Sewers or Wastewater treatment plant and might lead to a Not serious issue | BIOFOS |  | A flow sensor is deliberately broken and no data is received. The control software is made with fall-back in case of sensor failure. Sensor failure or no data or data flatline will trigger en alarm to a operator | 3,7,11,28,30 | 3: CameraSurveillance 7: BinaryContacts 11: DiscreetAppearance 26: ProcedureForPersonnelChanges 28: SecurityCheckOfEmployees 30: RedundantAssetsAndInfrastructures 51: AppropriateLayingOfWires
20 | External attacker | physical | Destruction | Sensors | DS11 Flow forecast | Sewers or Wastewater treatment plant | Not serious | External attacker generates a physical threat causing a Destruction of the Sensors of the DS11 Flow forecast which affects Sewers or Wastewater treatment plant and might lead to a Not serious issue | BIOFOS | revised by BIOFOS | An external attacker breaks into one of the buildings where several sensors is placed, during the burglary the external attacker breaks one or several sensors. The control software is made with fall-back in case of sensor failure. Sensor failure or no data or data flatline will trigger en alarm to a operator | 3,7,11,30 | 3: CameraSurveillance 7: BinaryContacts 11: DiscreetAppearance 30: RedundantAssetsAndInfrastructures 51: AppropriateLayingOfWires
21 | Internal attacker | cyber | Manipulation of the data | Server | DS11 Flow forecast | Sewers or Wastewater treatment plant | Quantity | Internal attacker generates a cyber threat causing a Manipulation of the data of the Server of the DS11 Flow forecast which affects Sewers or Wastewater treatment plant and might lead to a Quantity issue | BIOFOS |  | (An angry) BIOFOS employee is deliberately manipulating data to obtain bad treatment | 26,28,46, 48, 54,58,67,68 | 26: ProcedureForPersonnelChanges 28: SecurityCheckOfEmployees 46: RestrictedAccesToITSystem 48: CryptographicProcesses 54: DataIntegrityCheck 58: NetworkTrafficAnalysis 67: Authenticity check 68: Access control
22 | Internal attacker | cyber | Manipulation of the data | Server | DS11 Flow forecast | Sewers or Wastewater treatment plant | Quality | Internal attacker generates a cyber threat causing a Manipulation of the data of the Server of the DS11 Flow forecast which affects Sewers or Wastewater treatment plant and might lead to a Quality issue | BIOFOS | Not the same as 21, different consequence | (An angry) BIOFOS employee is deliberately manipulating data to obtain bad treatment | 26,28,46, 48, 54,58,67,68 | 26: ProcedureForPersonnelChanges 28: SecurityCheckOfEmployees 46: RestrictedAccesToITSystem 48: CryptographicProcesses 54: DataIntegrityCheck 58: NetworkTrafficAnalysis 67: Authenticity check 68: Access control
23 | External supplier | cyber | Manipulation of the data | Server | DS11 Flow forecast | Sewers or Wastewater treatment plant | Quantity | External supplier generates a cyber threat causing a Manipulation of the data of the Server of the DS11 Flow forecast which affects Sewers or Wastewater treatment plant and might lead to a Quantity issue | BIOFOS |  | An external supplier perhaps loosing a new tender, is deliberately manipulating data to obtain bad treatment | 46, 48, 54,58,67,68 | 46: RestrictedAccesToITSystem 48: CryptographicProcesses 54: DataIntegrityCheck 58: NetworkTrafficAnalysis 67: Authenticity check 68: Access control
24 | External supplier | cyber | Manipulation of the data | Server | DS11 Flow forecast | Sewers or Wastewater treatment plant | Quality | External supplier generates a cyber threat causing a Manipulation of the data of the Server of the DS11 Flow forecast which affects Sewers or Wastewater treatment plant and might lead to a Quality issue | BIOFOS | Not the same as 23, different consequence | An external supplier perhaps loosing a new tender, is deliberately manipulating data to obtain bad treatment | 46, 48, 54,58,67,68 | 46: RestrictedAccesToITSystem 48: CryptographicProcesses 54: DataIntegrityCheck 58: NetworkTrafficAnalysis 67: Authenticity check 68: Access control
25 | Human fault | cyber | Manipulation of the data | Server | DS11 Flow forecast | Sewers or Wastewater treatment plant | Quantity | Human fault generates a cyber threat causing a Manipulation of the data of the Server of the DS11 Flow forecast which affects Sewers or Wastewater treatment plant and might lead to a Quantity issue | BIOFOS |  | An attacker use the ALERT system to access data from the solutions | 27,44, 45, 46, 50 | 27: EmployeesTrainings 44: Password security 45: TwoFactorAuthentification 46: RestrictedAccesToITSystem 50: NetworkSeparation
26 | Human fault | cyber | Manipulation of the data | Server | DS11 Flow forecast | Sewers or Wastewater treatment plant | Quality | Human fault generates a cyber threat causing a Manipulation of the data of the Server of the DS11 Flow forecast which affects Sewers or Wastewater treatment plant and might lead to a Quality issue | BIOFOS | Not the same as 25, different consequence | An attacker use the ALERT system to access data from the solutions | 27,44, 45, 46, 50 | 27: EmployeesTrainings 44: Password security 45: TwoFactorAuthentification 46: RestrictedAccesToITSystem 50: NetworkSeparation
27 | External Attacker | cyber | manipulation of the data | ALERT SYSTEM | Early Warning System for bathing water quality | Digital solution users | False information | External Attacker generates a cyber threat causing a manipulation of the data of the ALERT SYSTEM of the Early Warning System for bathing water quality which affects Digital solution users and might lead to a False information issue | SIAAP |  | Some accesses the ML Based early warning system and modifiy the data | 26, 27, 28, 29, 30, 48,54,58,67,68
28 | External Attacker | cyber | manipulation of the data | ALERT SYSTEM | Early Warning System for bathing water quality | Digital solution users | Information leak | External Attacker generates a cyber threat causing a manipulation of the data of the ALERT SYSTEM of the Early Warning System for bathing water quality which affects Digital solution users and might lead to a Information leak issue | SIAAP |  | Some accesses the ML Based early warning system and modifiy the data | 26, 27, 28, 29, 30, 48,54,58,67,68
29 | External Attacker | cyber | Manipulation of the data | ML Based Early warning system for bathing water | Early Warning System for bathing water quality | Digital solution users | False information | External Attacker generates a cyber threat causing a Manipulation of the data of the ML Based Early warning system for bathing water of the Early Warning System for bathing water quality which affects Digital solution users and might lead to a False information issue | SIAAP |  | Some accesses the ML Based early warning system and modifiy the data | 26, 27, 28, 29, 48, 54, 58, 67, 68
30 | External Attacker | cyber | Manipulation of the data | ML Based Early warning system for bathing water | Early Warning System for bathing water quality | Digital solution users | Reputation | External Attacker generates a cyber threat causing a Manipulation of the data of the ML Based Early warning system for bathing water of the Early Warning System for bathing water quality which affects Digital solution users and might lead to a Reputation issue | SIAAP | revised by SIAAP | An attacker gets access to the Early Warning System and sent wrong quality data to the users preventing them from making a right decision on the opening or closing of a bathing site. Thus, making them doubt the EWS | 26, 27, 28, 29, 48, 54, 58, 67, 68
31 | External Attacker | cyber | Manipulation of the data | ML Based Early warning system for bathing water | Early Warning System for bathing water quality | Digital solution users | Health issues | External Attacker generates a cyber threat causing a Manipulation of the data of the ML Based Early warning system for bathing water of the Early Warning System for bathing water quality which affects Digital solution users and might lead to a Health issues issue | SIAAP | revised by SIAAP | If the users decides to open a bathing site based on wrong information, it will lead to people bathing in water that does not have a good quality, causing health issues | 26, 27, 28, 29, 48, 54, 58, 67, 68
32 | External Attacker | cyber | Denial of Service | Sensors | Early Warning System for safe water reuse | Irrigation water | Quality | External Attacker generates a cyber threat causing a Denial of Service of the Sensors of the Early Warning System for safe water reuse which affects Irrigation water and might lead to a Quality issue | SINTEF |  | An attacker might manipulate the Early Warning system's data, therefore generating warnings not related to the actual water quality. The latter would lead to water reuse quality issues and/or wastewater tratment plant reputation impacts. | 1, 3, 30, 58, 59, 69, 71
33 | External Attacker | cyber | Manipulation of the data | Sensors | Early Warning System for safe water reuse | Irrigation water | Quality | External Attacker generates a cyber threat causing a Manipulation of the data of the Sensors of the Early Warning System for safe water reuse which affects Irrigation water and might lead to a Quality issue | SINTEF |  | An attacker might manipulate the Early Warning system's data, therefore generating warnings not related to the actual water quality. The latter would lead to water reuse quality issues and/or wastewater tratment plant reputation impacts. | 1, 3, 27, 30, 46, 48, 54, 67
34 | External Attacker | cyber | Manipulation | Server | Early Warning System for safe water reuse | Irrigation water | Quality | External Attacker generates a cyber threat causing a Manipulation of the Server of the Early Warning System for safe water reuse which affects Irrigation water and might lead to a Quality issue | CAP-UNIVPM | CAP Should check example | An attacker might want to manipulate the data by attacking the MQTT server (by default, MQTT does not provide any security mechanism). | 46, 48, 54, 67, 68
35 | External Attacker | cyber | Manipulation | Server | Early Warning System for safe water reuse | Irrigation water | Health issues | External Attacker generates a cyber threat causing a Manipulation of the Server of the Early Warning System for safe water reuse which affects Irrigation water and might lead to a Health issues issue | CAP-UNIVPM | CAP Should check example | An attacker might want to manipulate the data by attacking the MQTT server (by default, MQTT does not provide any security mechanism). | 46, 48, 54, 67, 68
36 | Internal Attacker | cyber | Manipulation | Server | Early Warning System for safe water reuse | Irrigation water | Reputation | Internal Attacker generates a cyber threat causing a Manipulation of the Server of the Early Warning System for safe water reuse which affects Irrigation water and might lead to a Reputation issue | CAP-UNIVPM | CAP Should check example | An internal attacker might manipulate the Early Warning system's data in order to avoid compliance problems. | 27,46, 48, 50, 54,58,67,68
37 | Internal Attacker | cyber | Manipulation | Server | Early Warning System for safe water reuse | Irrigation water | Quality | Internal Attacker generates a cyber threat causing a Manipulation of the Server of the Early Warning System for safe water reuse which affects Irrigation water and might lead to a Quality issue | CAP-UNIVPM | CAP Should check example | An internal attacker might manipulate the Early Warning system's data in order to avoid compliance problems. | 27,46, 48, 50, 54,58,67,68
38 | External Attacker | cyber | Manipulation of the data | Sensors | Match-making tool | Digital solution users | Quantity | External Attacker generates a cyber threat causing a Manipulation of the data of the Sensors of the Match-making tool which affects Digital solution users and might lead to a Quantity issue | SINTEF |  | An attacker attacks MQTT, and act as publisher, polluting the real data. | 27, 30, 46, 48, 54, 58, 59, 67, 72
39 | External Attacker | cyber | Manipulation of the data | Sensors | Match-making tool | Digital solution users | Quality | External Attacker generates a cyber threat causing a Manipulation of the data of the Sensors of the Match-making tool which affects Digital solution users and might lead to a Quality issue | SINTEF |  | An attacker attacks MQTT, and act as publisher, polluting the real data. | 27, 30, 46, 48, 54, 58, 59, 67, 72
40 | External Attacker | cyber | Denial of Service | Server | Match-making tool | Digital solution users | Quantity | External Attacker generates a cyber threat causing a Denial of Service of the Server of the Match-making tool which affects Digital solution users and might lead to a Quantity issue | SINTEF | CAP Should check example | An attacker attacks MQTT, and act as publisher, polluting the real data. | 30, 58, 66
41 | External Attacker | cyber | Denial of Service | Server | Match-making tool | Digital solution users | Quality | External Attacker generates a cyber threat causing a Denial of Service of the Server of the Match-making tool which affects Digital solution users and might lead to a Quality issue | SINTEF | CAP Should check example | An attacker attacks MQTT, and act as publisher, polluting the real data. | 30, 58, 66
42 | External Attacker | cyber | Manipulation of the data | Server | Match-making tool | Digital solution users | Damage to stakeholder activtiy | External Attacker generates a cyber threat causing a Manipulation of the data of the Server of the Match-making tool which affects Digital solution users and might lead to a Damage to stakeholder activtiy issue | CAP-UNIVPM |  | An user has acces to the server and enters wrong or incorrect values which triggers an alert, tricking the ML Algorithm into issuing a warning; leading to quality and quantity issues of the reuse water. | 27, 44, 45, 46, 48, 54, 67, 68
43 | External Attacker | cyber | Manipulation of the data | Server | Match-making tool | Digital solution users | Reputation | External Attacker generates a cyber threat causing a Manipulation of the data of the Server of the Match-making tool which affects Digital solution users and might lead to a Reputation issue | CAP-UNIVPM |  | An user has acces to the server and enters wrong or incorrect values which triggers an alert, tricking the ML Algorithm into issuing a warning; leading to quality and quantity issues of the reuse water. | 27, 44, 45, 46, 48, 54, 67, 68
44 | External Attacker | cyber | Manipulation of the data | Web application | Match-making tool | Digital solution users | Information Leak | External Attacker generates a cyber threat causing a Manipulation of the data of the Web application of the Match-making tool which affects Digital solution users and might lead to a Information Leak issue | CAP-UNIVPM | CAP Should check example | An external attacker might get sensible information on the users of the Match-making tool | 27, 44, 45, 46, 48, 54, 67, 68
45 | Human fault | Cyber | Manipulation of the data | Server | ML Based Early warning system for bathing water | Raw water bodies | Quality | Human fault generates a Cyber threat causing a Manipulation of the data of the Server of the ML Based Early warning system for bathing water which affects Raw water bodies and might lead to a Quality issue | SIAAP | revised by SIAAP | The data used to calibrate the EWS for a specific bathing site is incorrect, leading to false prevention of the water quality | 44, 46, 50
46 | External Attacker | cyber | Manipulation of the data | Web applicaton | Mobile Apps to communicate bathing water quality | Digital solution users | False information | External Attacker generates a cyber threat causing a Manipulation of the data of the Web applicaton of the Mobile Apps to communicate bathing water quality which affects Digital solution users and might lead to a False information issue | SIAAP |  | Someone can access the expert app or the public app and change the status of the bathing | 44, 45, 46, 48, 54, 68, 70
47 | External Attacker | cyber | Manipulation of the data | Web applicaton | Mobile Apps to communicate bathing water quality | Digital solution users | Health issues | External Attacker generates a cyber threat causing a Manipulation of the data of the Web applicaton of the Mobile Apps to communicate bathing water quality which affects Digital solution users and might lead to a Health issues issue | SIAAP | revised by SIAAP | An attacker access the mobile app and changes the status of a bathing site from "closed" to "open" leading people to swim in a bad quality water | 44, 45, 46, 48, 54, 68, 70
48 | External Attacker | cyber | Manipulation of the data | Web applicaton | Mobile Apps to communicate bathing water quality | Digital solution users | Reputation | External Attacker generates a cyber threat causing a Manipulation of the data of the Web applicaton of the Mobile Apps to communicate bathing water quality which affects Digital solution users and might lead to a Reputation issue | SIAAP | revised by SIAAP | An attacker access the mobile app and changes the status of a bathing site from "closed" to "open" leading people to swim in a bad quality water. People will then not trust the information coming from the app | 44, 45, 46, 48, 54, 68, 70
49 | External Attacker | cyber | manipulation of the data | Cloud | mobile sensor (temperature, conductivity) | Sewer system | Reputation | External Attacker generates a cyber threat causing a manipulation of the data of the Cloud of the mobile sensor (temperature, conductivity) which affects Sewer system and might lead to a Reputation issue | BWB | Missing example - Need more info on the Berlin case |  | 44, 46, 50
50 | Operator | Human failure | missing data | Cloud | mobile sensor (temperature, conductivity) | Sewer system | CSO | Operator generates a Human failure threat causing a missing data of the Cloud of the mobile sensor (temperature, conductivity) which affects Sewer system and might lead to a CSO issue | BWB | Missing example - Need more info on the Berlin case |  | 27, 30, 49
51 | External Attacker | cyber | Denial of Service | Web server | Serious Game | Digital solution users | Reputation | External Attacker generates a cyber threat causing a Denial of Service of the Web server of the Serious Game which affects Digital solution users and might lead to a Reputation issue | SINTEF |  | An attacker exploits a vulnerability on the server and defaces the web page. | 49, 57, 60, 63, 64, 70
52 | Internal attacker | cyber | Manipulation | Web server | Serious Game | Digital solution users | Reputation | Internal attacker generates a cyber threat causing a Manipulation of the Web server of the Serious Game which affects Digital solution users and might lead to a Reputation issue | SINTEF |  | An employee edits the data of the offline sensors before uploading it to the web platform, resulting in misleading results. | 26, 27, 28, 44, 46, 48, 54, 67, 68
53 | Internal attacker | cyber | Denial of Service | Web server | Serious Game | Digital solution users | Reputation | Internal attacker generates a cyber threat causing a Denial of Service of the Web server of the Serious Game which affects Digital solution users and might lead to a Reputation issue | SINTEF |  | An angry employee edits the code of the game, preventing it from working once deployed. | 57, 60, 73
54 | Internal attacker | cyber | Manipulation of the data | Sensors | Temperature sensor Web-Platform | CSOs data quality | Financial | Internal attacker generates a cyber threat causing a Manipulation of the data of the Sensors of the Temperature sensor Web-Platform which affects CSOs data quality and might lead to a Financial issue | SINTEF | Missing example - Need more information on the sensors (from Sofia) |  | 27, 28, 46, 48, 54, 67
55 | Internal attacker | cyber | Manipulation of the data | Sensors | Temperature sensor Web-Platform | CSOs data quality | Quality | Internal attacker generates a cyber threat causing a Manipulation of the data of the Sensors of the Temperature sensor Web-Platform which affects CSOs data quality and might lead to a Quality issue | SINTEF | Missing example - Need more information on the sensors (from Sofia) |  | 27, 28, 46, 48, 54, 67
56 | Internal attacker | cyber | Manipulation of the data | Sensors | Temperature sensor Web-Platform | CSOs data quality | Reputation | Internal attacker generates a cyber threat causing a Manipulation of the data of the Sensors of the Temperature sensor Web-Platform which affects CSOs data quality and might lead to a Reputation issue | SINTEF | Missing example - Need more information on the sensors (from Sofia) |  | 27, 28, 46, 48, 54, 67
57 | External Attacker | cyber | Manipulation of the data | Sensors | Temperature sensor Web-Platform | CSOs data quality | Financial | External Attacker generates a cyber threat causing a Manipulation of the data of the Sensors of the Temperature sensor Web-Platform which affects CSOs data quality and might lead to a Financial issue | SINTEF | Making the asumptions that the sensors are either physically accessible by an external attacker, or that they communicate wirelessly | An attacker access the sensors, and manipualte the data to trick the system into thinking that there has been an illicit connection (or to hide one), thus leading to the dispatch of a team (or not). | 46, 48, 54, 67
58 | External Attacker | cyber | Manipulation of the data | Sensors | Temperature sensor Web-Platform | CSOs data quality | Quality | External Attacker generates a cyber threat causing a Manipulation of the data of the Sensors of the Temperature sensor Web-Platform which affects CSOs data quality and might lead to a Quality issue | SINTEF | Making the asumptions that the sensors are either physically accessible by an external attacker, or that they communicate wirelessly | An attacker access the sensors, and manipualte the data to trick the system into thinking that there has been an illicit connection (or to hide one), thus leading to the dispatch of a team (or not). | 46, 48, 54, 67
59 | External Attacker | cyber | Manipulation of the data | Sensors | Temperature sensor Web-Platform | CSOs data quality | Reputation | External Attacker generates a cyber threat causing a Manipulation of the data of the Sensors of the Temperature sensor Web-Platform which affects CSOs data quality and might lead to a Reputation issue | SINTEF | Making the asumptions that the sensors are either physically accessible by an external attacker, or that they communicate wirelessly | An attacker access the sensors, and manipualte the data to trick the system into thinking that there has been an illicit connection (or to hide one), thus leading to the dispatch of a team (or not). | 46, 48, 54, 67
60 | External Attacker | cyber | Denial of Service | Sensors | Temperature sensor Web-Platform | CSOs data quality | Financial | External Attacker generates a cyber threat causing a Denial of Service of the Sensors of the Temperature sensor Web-Platform which affects CSOs data quality and might lead to a Financial issue | SINTEF | Need check from Sofia | An attacker jams the signals for the online sensors, preventing them to send their data to the server. | 30, 58, 66, 69
61 | External Attacker | cyber | Denial of Service | Sensors | Temperature sensor Web-Platform | CSOs data quality | Quality | External Attacker generates a cyber threat causing a Denial of Service of the Sensors of the Temperature sensor Web-Platform which affects CSOs data quality and might lead to a Quality issue | SINTEF | Need check from Sofia | An attacker jams the signals for the online sensors, preventing them to send their data to the server. | 30, 58, 66, 69
62 | External Attacker | cyber | Spoofing | Web application | Temperature sensor Web-Platform | CSOs data quality | Financial | External Attacker generates a cyber threat causing a Spoofing of the Web application of the Temperature sensor Web-Platform which affects CSOs data quality and might lead to a Financial issue | SINTEF | Need check from Sofia | An attacker manages to spoof an online sensor and upload misleading data to the web platform | 27
63 | External Attacker | cyber | Spoofing | Web application | Temperature sensor Web-Platform | CSOs data quality | Quality | External Attacker generates a cyber threat causing a Spoofing of the Web application of the Temperature sensor Web-Platform which affects CSOs data quality and might lead to a Quality issue | SINTEF | Need check from Sofia | An attacker manages to spoof an online sensor and upload misleading data to the web platform | 27
64 | External Attacker | cyber | Manipulation of the data | Sensors | Web Platorm (Berlin) | Sewer system | Financial | External Attacker generates a cyber threat causing a Manipulation of the data of the Sensors of the Web Platorm (Berlin) which affects Sewer system and might lead to a Financial issue | SINTEF | Missing example - Need more info on the Berlin case |  | 46, 48, 54, 67
65 | External Attacker | cyber | Manipulation of the data | Sensors | Web Platorm (Berlin) | Sewer system | Quality | External Attacker generates a cyber threat causing a Manipulation of the data of the Sensors of the Web Platorm (Berlin) which affects Sewer system and might lead to a Quality issue | SINTEF | Missing example - Need more info on the Berlin case |  | 46, 48, 54, 67
66 | External Attacker | cyber | Manipulation of the data | Server | Temperature sensor Web-Platform | CSOs data quality | Financial | External Attacker generates a cyber threat causing a Manipulation of the data of the Server of the Temperature sensor Web-Platform which affects CSOs data quality and might lead to a Financial issue | Sofiyska voda, DS15 - proposed by Sewer Project manager | Missing example - Need more information on the solution (from Sofia) |  | 46, 48, 54, 67, 68
67 | Internal attacker | cyber | Eavesdropping | Server | Well-Diary | Operator | Information Leak | Internal attacker generates a cyber threat causing a Eavesdropping of the Server of the Well-Diary which affects Operator and might lead to a Information Leak issue | SINTEF | Need check from Berlin | An attacker exploits missing access controls on the application/API to gain access to personnal information of operators, and to other information such as real time position. | 46, 48, 68
68 | Human fault | cyber | Manipulation of the data | Server | ALERT SYSTEM | Raw water bodies | False information | Human fault generates a cyber threat causing a Manipulation of the data of the Server of the ALERT SYSTEM which affects Raw water bodies and might lead to a False information issue | SINTEF |  | The access control is compromised by error (someone gives access to someone else by error for instance) | 26, 27, 28, 29, 68, 44, 46
69 | Human fault | cyber | Manipulation of the data | Server | ALERT SYSTEM | Raw water bodies | Information Leak | Human fault generates a cyber threat causing a Manipulation of the data of the Server of the ALERT SYSTEM which affects Raw water bodies and might lead to a Information Leak issue | SINTEF |  | The access control is compromised by error (someone gives access to someone else by error for instance) | 26, 27, 28, 29, 68, 44, 46
70 | Human fault | cyber | Manipulation of the data | Server | ALERT SYSTEM | Raw water bodies | Information leak | Human fault generates a cyber threat causing a Manipulation of the data of the Server of the ALERT SYSTEM which affects Raw water bodies and might lead to a Information leak issue | SINTEF |  | API credentials are issued to the wrong "person" giving access to data | 26, 27, 28, 29, 46, 68
71 | Human fault | cyber | Manipulation of the data | Server | ALERT SYSTEM | Raw water bodies | False information | Human fault generates a cyber threat causing a Manipulation of the data of the Server of the ALERT SYSTEM which affects Raw water bodies and might lead to a False information issue | SINTEF |  | API credentials are issued to the wrong "person" giving access to data | 26, 27, 28, 29, 46, 68
72 | Human fault | cyber | Denial of Service | Server | ALERT SYSTEM | Raw water bodies | Quality | Human fault generates a cyber threat causing a Denial of Service of the Server of the ALERT SYSTEM which affects Raw water bodies and might lead to a Quality issue | SINTEF |  | API credentials are issued to the wrong "person" giving access to data | 26, 27, 28, 29, 46, 68
73 | Human fault | cyber | Denial of Service | Server | ALERT SYSTEM | Raw water bodies | Reputation | Human fault generates a cyber threat causing a Denial of Service of the Server of the ALERT SYSTEM which affects Raw water bodies and might lead to a Reputation issue | SINTEF |  | API credentials are issued to the wrong "person" giving access to data | 26, 27, 28, 29, 46, 68
74 | External Attacker | cyber | Denial of Service | Web server | Serious Game | Digital solution users | Reputation | External Attacker generates a cyber threat causing a Denial of Service of the Web server of the Serious Game which affects Digital solution users and might lead to a Reputation issue | SINTEF |  | An attacker DDOS the server | 30, 66
48 | [7 empty] | generates a threat causing a of the of the which affects and might lead to a issue
49 | [7 empty] | generates a threat causing a of the of the which affects and might lead to a issue
50 | [7 empty] | generates a threat causing a of the of the which affects and might lead to a issue
51 | [7 empty] | generates a threat causing a of the of the which affects and might lead to a issue
52 | [7 empty] | generates a threat causing a of the of the which affects and might lead to a issue
53 | [7 empty] | generates a threat causing a of the of the which affects and might lead to a issue
54 | [7 empty] | generates a threat causing a of the of the which affects and might lead to a issue
55 | [7 empty] | generates a threat causing a of the of the which affects and might lead to a issue
56 | [7 empty] | generates a threat causing a of the of the which affects and might lead to a issue
57 | [7 empty] | generates a threat causing a of the of the which affects and might lead to a issue
58 | [7 empty] | generates a threat causing a of the of the which affects and might lead to a issue
59 | [7 empty] | generates a threat causing a of the of the which affects and might lead to a issue
60 | [7 empty] | generates a threat causing a of the of the which affects and might lead to a issue
61 | [7 empty] | generates a threat causing a of the of the which affects and might lead to a issue
62 | [7 empty] | generates a threat causing a of the of the which affects and might lead to a issue
63 | [7 empty] | generates a threat causing a of the of the which affects and might lead to a issue
64 | [7 empty] | generates a threat causing a of the of the which affects and might lead to a issue
65 | [7 empty] | generates a threat causing a of the of the which affects and might lead to a issue
66 | [7 empty] | generates a threat causing a of the of the which affects and might lead to a issue
67 | [7 empty] | generates a threat causing a of the of the which affects and might lead to a issue
68 | [7 empty] | generates a threat causing a of the of the which affects and might lead to a issue
69 | [7 empty] | generates a threat causing a of the of the which affects and might lead to a issue
70 | [7 empty] | generates a threat causing a of the of the which affects and might lead to a issue
71 | [7 empty] | generates a threat causing a of the of the which affects and might lead to a issue
72 | [7 empty] | generates a threat causing a of the of the which affects and might lead to a issue
73 | [7 empty] | generates a threat causing a of the of the which affects and might lead to a issue
74 | [7 empty] | generates a threat causing a of the of the which affects and might lead to a issue
75 | [7 empty] | generates a threat causing a of the of the which affects and might lead to a issue
76 | [7 empty] | generates a threat causing a of the of the which affects and might lead to a issue
77 | [7 empty] | generates a threat causing a of the of the which affects and might lead to a issue
78 | [7 empty] | generates a threat causing a of the of the which affects and might lead to a issue
79 | [7 empty] | generates a threat causing a of the of the which affects and might lead to a issue
Note on K34: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Are the two examples swapped?

## DWC - Options
COMPLEMENT the PROPOSED options on need BASED ON DWC DOMAIN
Type of source | Type of threat | Type of event | Supportings asset | Composite supporting asset | Primary Asset | Consequence dimension
External attacker | Cyber | Eavesdropping | Sensors | ALERT system | Catchment area | Financial
External supplier | Cyber-physical | Denial of Service | Servers | ML Based Early warning system for bathing water | Drinking water network | Quality
Human fault | Physical | Manipulation | Web application | Early warning system for safe water reuse | Drinking water tanks | Quantity
Internal attacker |  | Spoofing | Database | Match-making tool | Pressure boosting station | Reputation
|  | Destruction | Web API |  | Raw water bodies | Information leak
|  |  | Communication medium (GPRS, LoRaWAN, etc.) |  | Wastewater treatment plant | Health issues
|  |  | Mobile application |  | Water abstraction points | False information
|  |  | Unmanned Aerial Vehicle |  | Water treatment plants | Not serious
|  |  | Data from [composite supporting asset] |  | Irrigation water | Damage to stakeholders activity
Digital solution users